## PR_Calc
PR CALCULATION
02 MAGGIO 2026 | [67 empty] | 2 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 51
RAW PR | [64 empty] | 0.82461 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 82.4615
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 82.5189
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 58.5127
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-02 | 00:00:00.000 | -2 | -0.0005 | -1.6 | -0.0004 | -0.00045 | 0 | -0.00045 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8312.2
2026-05-02 | 00:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 00:30:00.000 | -0.7 | -0.000175 | 0 | 0 | -8.75e-05 | 0 | -8.75e-05 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 00:45:00.000 | -1.6 | -0.0004 | 0 | 0 | -0.0002 | 0 | -0.0002 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 01:00:00.000 | -1.9 | -0.000475 | -0.9 | -0.000225 | -0.00035 | 0 | -0.00035 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 01:15:00.000 | -2 | -0.0005 | -1.7 | -0.000425 | -0.0004625 | 0 | -0.0004625 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 01:30:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 01:45:00.000 | -2 | -0.0005 | -1.5 | -0.000375 | -0.0004375 | 0 | -0.0004375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 02:00:00.000 | -1.9 | -0.000475 | -1.6 | -0.0004 | -0.0004375 | 0 | -0.0004375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 02:15:00.000 | -2 | -0.0005 | -1.8 | -0.00045 | -0.000475 | 0 | -0.000475 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 02:30:00.000 | -2 | -0.0005 | -1.8 | -0.00045 | -0.000475 | 0 | -0.000475 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 02:45:00.000 | -2.2 | -0.00055 | -1.7 | -0.000425 | -0.0004875 | 0 | -0.0004875 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 03:00:00.000 | -1.5 | -0.000375 | -0.4 | -0.0001 | -0.0002375 | 0 | -0.0002375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 03:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 03:30:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 03:45:00.000 | -1.7 | -0.000425 | -1 | -0.00025 | -0.0003375 | 0 | -0.0003375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 04:00:00.000 | -2 | -0.0005 | -1.3 | -0.000325 | -0.0004125 | 0 | -0.0004125 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 04:15:00.000 | -2 | -0.0005 | -2.4 | -0.0006 | -0.00055 | 0 | -0.00055 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 04:30:00.000 | -2.4 | -0.0006 | -2.3 | -0.000575 | -0.0005875 | 0 | -0.0005875 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 04:45:00.000 | -2.7 | -0.000675 | -3 | -0.00075 | -0.0007125 | 0 | -0.0007125 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 05:00:00.000 | -1.3 | -0.000325 | -1.4 | -0.00035 | -0.0003375 | 0 | -0.0003375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 05:15:00.000 | -1.7 | -0.000425 | -1 | -0.00025 | -0.0003375 | 0 | -0.0003375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 05:30:00.000 | -0.9 | -0.000225 | -1.4 | -0.00035 | -0.0002875 | 0 | -0.0002875 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 05:45:00.000 | -1 | -0.00025 | -1.3 | -0.000325 | -0.0002875 | 0 | -0.0002875 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 06:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 06:15:00.000 | 0.8 | 0.0002 | 1.1 | 0.000275 | 0.0002375 | 0 | 0.0002375 | 0.31579 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 06:30:00.000 | 12.2 | 0.00305 | 11.1 | 0.002775 | 0.0029125 | 0 | 0.0029125 | 0.094421 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 06:45:00.000 | 45.9 | 0.011475 | 44.3 | 0.011075 | 0.011275 | 0 | 0.011275 | 0.035477 | 30141.3 | 30141.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 07:00:00.000 | 100.4 | 0.0251 | 102.3 | 0.025575 | 0.025337 | 101.35 | 0.025575 | 0.018747 | 30141.4 | 30141.5 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 07:15:00.000 | 180.4 | 0.0451 | 186.5 | 0.046625 | 0.045863 | 183.45 | 0.046625 | 0.033252 | 30141.5 | 30141.8 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 07:30:00.000 | 276.5 | 0.069125 | 279 | 0.06975 | 0.069438 | 277.75 | 0.06975 | 0.0090009 | 30141.8 | 30142.4 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 07:45:00.000 | 377.6 | 0.0944 | 373.6 | 0.0934 | 0.0939 | 375.6 | 0.0944 | 0.01065 | 30142.4 | 30143.3 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 08:00:00.000 | 479.9 | 0.11997 | 471.4 | 0.11785 | 0.11891 | 475.65 | 0.11997 | 0.01787 | 30143.3 | 30144.5 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 08:15:00.000 | 580.1 | 0.14503 | 576.5 | 0.14413 | 0.14458 | 578.3 | 0.14503 | 0.0062251 | 30144.5 | 30146 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 08:30:00.000 | 681 | 0.17025 | 681.8 | 0.17045 | 0.17035 | 681.4 | 0.17045 | 0.0011741 | 30146 | 30147.8 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 08:45:00.000 | 778.5 | 0.19462 | 786.2 | 0.19655 | 0.19559 | 782.35 | 0.19655 | 0.0098421 | 30147.8 | 30149.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 09:00:00.000 | 888 | 0.222 | 888.7 | 0.22218 | 0.22209 | 888.35 | 0.22218 | 0.00078798 | 30149.9 | 30152.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 09:15:00.000 | 949.7 | 0.23743 | 941 | 0.23525 | 0.23634 | 945.35 | 0.23743 | 0.0092029 | 30152.2 | 30154.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 09:30:00.000 | 966.1 | 0.24153 | 957.1 | 0.23928 | 0.2404 | 961.6 | 0.24153 | 0.0093594 | 30154.7 | 30157.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 09:45:00.000 | 972.8 | 0.2432 | 962.1 | 0.24053 | 0.24186 | 967.45 | 0.2432 | 0.01106 | 30157.2 | 30159.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 10:00:00.000 | 980.6 | 0.24515 | 968.2 | 0.24205 | 0.2436 | 974.4 | 0.24515 | 0.012726 | 30159.7 | 30162.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 10:15:00.000 | 984.4 | 0.2461 | 969.6 | 0.2424 | 0.24425 | 977 | 0.2461 | 0.015148 | 30162.2 | 30164.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 10:30:00.000 | 995.8 | 0.24895 | 978.5 | 0.24463 | 0.24679 | 987.15 | 0.24895 | 0.017525 | 30164.7 | 30167.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 10:45:00.000 | 996.4 | 0.2491 | 977.1 | 0.24427 | 0.24669 | 986.75 | 0.2491 | 0.019559 | 30167.2 | 30169.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 11:00:00.000 | 997.8 | 0.24945 | 977.4 | 0.24435 | 0.2469 | 987.6 | 0.24945 | 0.020656 | 30169.6 | 30171.8 | 2200 | 0.6572 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 210.048 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 210.048 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 17.504 | 210.048 | 0.68149
2026-05-02 | 11:15:00.000 | 998.4 | 0.2496 | 976.7 | 0.24418 | 0.24689 | 987.55 | 0.2496 | 0.021974 | 30171.8 | 30173.2 | 1400 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 11:30:00.000 | 998.4 | 0.2496 | 976.9 | 0.24422 | 0.24691 | 987.65 | 0.2496 | 0.021769 | 30173.2 | 30173.8 | 600 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 11:45:00.000 | 996.8 | 0.2492 | 974.8 | 0.2437 | 0.24645 | 985.8 | 0.2492 | 0.022317 | 30173.8 | 30174.4 | 600 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 12:00:00.000 | 995.5 | 0.24888 | 972.4 | 0.2431 | 0.24599 | 983.95 | 0.24888 | 0.023477 | 30174.4 | 30175 | 600 | 0.2005 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 0.68149
2026-05-02 | 12:15:00.000 | 998 | 0.2495 | 973.3 | 0.24332 | 0.24641 | 985.65 | 0.2495 | 0.02506 | 30175 | 30175.6 | 600 | 0.2005 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 0.68149
2026-05-02 | 12:30:00.000 | 991.1 | 0.24777 | 965.9 | 0.24147 | 0.24462 | 978.5 | 0.24777 | 0.025754 | 30175.6 | 30176.1 | 500 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 12:45:00.000 | 985 | 0.24625 | 949.8 | 0.23745 | 0.24185 | 967.4 | 0.24625 | 0.036386 | 30176.1 | 30176.7 | 600 | 0.2005 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 0.68149
2026-05-02 | 13:00:00.000 | 991.6 | 0.2479 | 965.7 | 0.24143 | 0.24466 | 978.65 | 0.2479 | 0.026465 | 30176.7 | 30177.3 | 600 | 0.2005 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 0.68149
2026-05-02 | 13:15:00.000 | 992.6 | 0.24815 | 966.1 | 0.24153 | 0.24484 | 979.35 | 0.24815 | 0.027059 | 30177.3 | 30177.9 | 600 | 0.2005 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 0.68149
2026-05-02 | 13:30:00.000 | 996.6 | 0.24915 | 970.6 | 0.24265 | 0.2459 | 983.6 | 0.24915 | 0.026434 | 30177.9 | 30178.5 | 600 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 13:45:00.000 | 994.3 | 0.24857 | 969.5 | 0.24238 | 0.24547 | 981.9 | 0.24857 | 0.025257 | 30178.5 | 30179.1 | 600 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 14:00:00.000 | 994.7 | 0.24868 | 971 | 0.24275 | 0.24571 | 982.85 | 0.24868 | 0.024114 | 30179.1 | 30179.6 | 500 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 14:15:00.000 | 1006.9 | 0.25172 | 983.6 | 0.2459 | 0.24881 | 995.25 | 0.25172 | 0.023411 | 30179.6 | 30180.2 | 600 | 0.2006 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 54.032 | 648.384 | 0.68149
2026-05-02 | 14:30:00.000 | 1005.8 | 0.25145 | 983.4 | 0.24585 | 0.24865 | 994.6 | 0.25145 | 0.022522 | 30180.2 | 30180.8 | 600 | 0.2005 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 0.68149
2026-05-02 | 14:45:00.000 | 1006 | 0.2515 | 983.4 | 0.24585 | 0.24867 | 994.7 | 0.2515 | 0.02272 | 30180.8 | 30181.4 | 600 | 0.2005 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 54.04 | 648.48 | 0.68149
2026-05-02 | 15:00:00.000 | 1012 | 0.253 | 990.5 | 0.24763 | 0.25031 | 1001.25 | 0.253 | 0.021473 | 30181.4 | 30182.3 | 900 | 0.5202 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 341.568 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 341.568 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 28.464 | 341.568 | 0.68149
2026-05-02 | 15:15:00.000 | 1015 | 0.25375 | 994.1 | 0.24852 | 0.25114 | 1004.55 | 0.25375 | 0.020805 | 30182.3 | 30183.9 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 15:30:00.000 | 1018.6 | 0.25465 | 997.7 | 0.24943 | 0.25204 | 1008.15 | 0.25465 | 0.020731 | 30183.9 | 30186.4 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 15:45:00.000 | 1015.8 | 0.25395 | 996.6 | 0.24915 | 0.25155 | 1006.2 | 0.25395 | 0.019082 | 30186.4 | 30188.8 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 16:00:00.000 | 1014.5 | 0.25362 | 993.4 | 0.24835 | 0.25099 | 1003.95 | 0.25362 | 0.021017 | 30188.8 | 30191.3 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 16:15:00.000 | 1016.4 | 0.2541 | 995.8 | 0.24895 | 0.25152 | 1006.1 | 0.2541 | 0.020475 | 30191.3 | 30193.8 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 16:30:00.000 | 1014.1 | 0.25353 | 992.6 | 0.24815 | 0.25084 | 1003.35 | 0.25353 | 0.021428 | 30193.8 | 30196.3 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 16:45:00.000 | 1009.8 | 0.25245 | 987.4 | 0.24685 | 0.24965 | 998.6 | 0.25245 | 0.022431 | 30196.3 | 30198.8 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 17:00:00.000 | 996.4 | 0.2491 | 974.8 | 0.2437 | 0.2464 | 985.6 | 0.2491 | 0.021916 | 30198.8 | 30201.3 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 17:15:00.000 | 937.4 | 0.23435 | 954.2 | 0.23855 | 0.23645 | 945.8 | 0.23855 | 0.017763 | 30201.3 | 30203.7 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 17:30:00.000 | 821.3 | 0.20532 | 869.5 | 0.21738 | 0.21135 | 845.4 | 0.21738 | 0.057014 | 30203.7 | 30206.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 17:45:00.000 | 711.7 | 0.17792 | 770.2 | 0.19255 | 0.18524 | 740.95 | 0.19255 | 0.078953 | 30206.2 | 30208.4 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 18:00:00.000 | 601 | 0.15025 | 667.9 | 0.16697 | 0.15861 | 634.45 | 0.16697 | 0.10545 | 30208.4 | 30210.3 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 18:15:00.000 | 490.3 | 0.12258 | 562 | 0.1405 | 0.13154 | 526.15 | 0.1405 | 0.13627 | 30210.3 | 30211.9 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 18:30:00.000 | 387.7 | 0.096925 | 457.4 | 0.11435 | 0.10564 | 422.55 | 0.11435 | 0.16495 | 30211.9 | 30213.2 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 18:45:00.000 | 283.3 | 0.070825 | 353.1 | 0.088275 | 0.07955 | 318.2 | 0.088275 | 0.21936 | 30213.2 | 30214.3 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 19:00:00.000 | 192 | 0.048 | 256.2 | 0.06405 | 0.056025 | 224.1 | 0.06405 | 0.28648 | 30214.3 | 30215 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 19:15:00.000 | 116.2 | 0.02905 | 170.2 | 0.04255 | 0.0358 | 143.2 | 0.04255 | 0.37709 | 30215 | 30215.4 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 19:30:00.000 | 54.5 | 0.013625 | 95.1 | 0.023775 | 0.0187 | 74.8 | 0.023775 | 0.54278 | 30215.4 | 30215.6 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 19:45:00.000 | 26.4 | 0.0066 | 33 | 0.00825 | 0.007425 | 0 | 0.007425 | 0.22222 | 30215.6 | 30215.7 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 20:00:00.000 | 6.2 | 0.00155 | 6.6 | 0.00165 | 0.0016 | 0 | 0.0016 | 0.0625 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 20:15:00.000 | -0.7 | -0.000175 | -0.5 | -0.000125 | -0.00015 | 0 | -0.00015 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 20:30:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 20:45:00.000 | -2.3 | -0.000575 | -2 | -0.0005 | -0.0005375 | 0 | -0.0005375 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 21:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 21:15:00.000 | -2.6 | -0.00065 | -2 | -0.0005 | -0.000575 | 0 | -0.000575 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 21:30:00.000 | -2 | -0.0005 | -1.4 | -0.00035 | -0.000425 | 0 | -0.000425 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 21:45:00.000 | -2 | -0.0005 | -1.5 | -0.000375 | -0.0004375 | 0 | -0.0004375 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 22:00:00.000 | -2 | -0.0005 | -1.4 | -0.00035 | -0.000425 | 0 | -0.000425 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 22:15:00.000 | -2.9 | -0.000725 | -2.4 | -0.0006 | -0.0006625 | 0 | -0.0006625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 22:30:00.000 | -3.1 | -0.000775 | -3 | -0.00075 | -0.0007625 | 0 | -0.0007625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 22:45:00.000 | -2.8 | -0.0007 | -3 | -0.00075 | -0.000725 | 0 | -0.000725 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 23:00:00.000 | -3 | -0.00075 | -3 | -0.00075 | -0.00075 | 0 | -0.00075 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 23:15:00.000 | -2.2 | -0.00055 | -2.3 | -0.000575 | -0.0005625 | 0 | -0.0005625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 23:30:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
2026-05-02 | 23:45:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68149
PR for each inverter |  |  | 10.2155 |  | 10.1931 | 10.2043 |  | 10.3626 |  |  |  | 74400 |  | 0.83711 | 0.83534 | 0.83809 | 0.83795 | 0.83861 | 0.83372 | 0.83324 | 0.81421 | 0.81088 | 0.81002 | 0.81124 | 0.83781 | #DIV/0! | #DIV/0! | #DIV/0! | 10278.048 | 0.8648 | 0.83274 | 0.8317 | 0.86422 | 0.86823 | 0.80144 | 0.83264 | 0.80197 | 0.80221 | 0.82833 | 0.79985 | 0.79995 |  |  |  | 10278.048 | 0.81861 | 0.81579 | 0.81111 | 0.81378 | 0.81273 | 0.81624 | 0.81549 | 0.81212 | 0.81337 | 0.81708 | 0.81624 | 0.87796 | #DIV/0! | #DIV/0! | #DIV/0! | 10278.048 |  | 0.82519 |  | #DIV/0! | #DIV/0! | 6.1113e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-02 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 06:30:00.000 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0.1 | 0.4 | 0.9 | 0 | 0 | 0 | 0.6 | 0.3 | 1.3 | 0 | 0 | 2.1 | 0 | 0 | 0 | 1.2 | 1.1 | 2.1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0
2026-05-02 | 06:45:00.000 | 7.5 | 6.5 | 7.7 | 7.2 | 8.3 | 6.9 | 7.5 | 7.2 | 8.6 | 7.3 | 8.2 | 8.8 | 7.6417 | 8.8 | 6.5 | 7.7 | 7.2 | 8.3 | 8.4 | 8 | 8.7 | 8.8 | 8.9 | 9.1 | 7.7 | 8.1 | 8.8 | 8.3083 | 9.1 | 7.2 | 7.9 | 6.6 | 7.3 | 7.2 | 7.3 | 9 | 8.6 | 7.6 | 7.1 | 6.7 | 7.7 | 7.5 | 7.5417 | 9 | 6.6
2026-05-02 | 07:00:00.000 | 21.4 | 21.3 | 23 | 22.7 | 22.9 | 21.5 | 21.4 | 21.1 | 22.2 | 22.3 | 23.2 | 22.9 | 22.1583 | 23.2 | 21.1 | 20.4 | 19.3 | 20.8 | 22 | 21.5 | 22.5 | 23 | 23.5 | 24.3 | 22.4 | 24.3 | 24 | 22.3333 | 24.3 | 19.3 | 24.5 | 20.7 | 22.7 | 24.3 | 23.9 | 26.4 | 25.7 | 25.4 | 23.8 | 20.6 | 25 | 24.3 | 23.9417 | 26.4 | 20.6
2026-05-02 | 07:15:00.000 | 46.4 | 46.3 | 49 | 47.9 | 48.3 | 46.3 | 45.4 | 46.7 | 47.8 | 47.7 | 49.7 | 48.5 | 47.5 | 49.7 | 45.4 | 43.6 | 42 | 44.2 | 46.3 | 45.7 | 48.1 | 48.2 | 49.4 | 51.3 | 47.9 | 51.3 | 50.3 | 47.3583 | 51.3 | 42 | 51.3 | 46.3 | 48.9 | 51.6 | 51.6 | 54.2 | 52.9 | 52.4 | 50.2 | 47.1 | 52.8 | 49.1 | 50.7 | 54.2 | 46.3
2026-05-02 | 07:30:00.000 | 78.1 | 77.8 | 80.4 | 79 | 79.3 | 77.3 | 76.3 | 80 | 80.5 | 80.2 | 82.3 | 80.7 | 79.325 | 82.3 | 76.3 | 73.4 | 72.4 | 74.7 | 76.2 | 75.6 | 80.1 | 79.3 | 81.6 | 83.8 | 78.9 | 84 | 82 | 78.5 | 84 | 72.4 | 85 | 79.3 | 82.6 | 85.8 | 84.7 | 88.2 | 86.1 | 85.3 | 83.3 | 79.9 | 86.3 | 80 | 83.875 | 88.2 | 79.3
2026-05-02 | 07:45:00.000 | 111.5 | 110.9 | 113.5 | 112.5 | 112.6 | 106.4 | 109.8 | 115.3 | 115.2 | 114.4 | 116.9 | 114.3 | 112.775 | 116.9 | 106.4 | 105.7 | 106.1 | 108.1 | 108.3 | 108.1 | 115.5 | 112.9 | 116.1 | 118.2 | 111.9 | 118.4 | 115.6 | 112.075 | 118.4 | 105.7 | 119.8 | 114.2 | 117.6 | 121 | 120.1 | 123.6 | 121.3 | 120 | 117.9 | 114.2 | 121.8 | 112.2 | 118.6417 | 123.6 | 112.2
2026-05-02 | 08:00:00.000 | 146.3 | 145.3 | 148.2 | 147.8 | 147.8 | 145.7 | 145.3 | 152.8 | 151.6 | 150.3 | 153 | 149.5 | 148.6333 | 153 | 145.3 | 139.7 | 141.8 | 137.8 | 141.9 | 142.2 | 152.7 | 142.5 | 152.5 | 153.9 | 146.4 | 154.4 | 150.7 | 146.375 | 154.4 | 137.8 | 155.5 | 150.6 | 154.1 | 157.7 | 156.8 | 159.9 | 158.7 | 155.8 | 154.1 | 150.5 | 158.2 | 145.1 | 154.75 | 159.9 | 145.1
2026-05-02 | 08:15:00.000 | 180.3 | 179.1 | 181.9 | 182.1 | 182.2 | 180.3 | 180.1 | 189.5 | 187.3 | 180.3 | 188.3 | 183.9 | 182.9417 | 189.5 | 179.1 | 172.6 | 176.6 | 177.5 | 168.4 | 175.2 | 188.8 | 182.2 | 187.9 | 188.6 | 180 | 189.3 | 185.5 | 181.05 | 189.3 | 168.4 | 191.2 | 187.2 | 190.7 | 194.4 | 193.6 | 196.1 | 195.8 | 191.4 | 190.3 | 187.1 | 194.3 | 177.7 | 190.8167 | 196.1 | 177.7
2026-05-02 | 08:30:00.000 | 214.4 | 212.9 | 215.5 | 215.9 | 215.7 | 213.9 | 214.7 | 225.8 | 222.6 | 221.1 | 223 | 209.5 | 217.0833 | 225.8 | 209.5 | 204.8 | 210.9 | 211.4 | 206.4 | 207.3 | 226 | 208.4 | 222.6 | 223 | 213 | 223.5 | 219.3 | 214.7167 | 226 | 204.8 | 226.2 | 223.9 | 226.7 | 230.4 | 222.2 | 231.7 | 232.3 | 226.5 | 226 | 223.5 | 230.1 | 210.5 | 225.8333 | 232.3 | 210.5
2026-05-02 | 08:45:00.000 | 245.7 | 243.8 | 246.4 | 247 | 246.4 | 245 | 246.1 | 259.1 | 255.3 | 253.8 | 254.9 | 248.7 | 249.35 | 259.1 | 243.8 | 226 | 242.4 | 242 | 226.5 | 236.7 | 257.7 | 245.7 | 253.8 | 253.8 | 243 | 254.6 | 250.2 | 244.3667 | 257.7 | 226 | 258.3 | 257.5 | 249.8 | 253.7 | 263 | 263.9 | 256.9 | 258.2 | 258.7 | 257.2 | 262.3 | 240 | 256.625 | 263.9 | 240
2026-05-02 | 09:00:00.000 | 275.2 | 273.6 | 275.4 | 275.9 | 275.3 | 274.6 | 275.7 | 281.2 | 280.4 | 279.5 | 279.9 | 276.6 | 276.9417 | 281.2 | 273.6 | 264.7 | 273.6 | 272.6 | 265.4 | 267.1 | 280.3 | 274.6 | 279.5 | 279.1 | 272.8 | 279.6 | 277.5 | 273.9 | 280.3 | 264.7 | 280.8 | 280.2 | 281.1 | 281.5 | 281.8 | 281.8 | 281.8 | 280.5 | 270.5 | 280.6 | 271.1 | 270.8 | 278.5417 | 281.8 | 270.5
2026-05-02 | 09:15:00.000 | 281.6 | 281.4 | 282 | 282.1 | 281.7 | 271.3 | 281.2 | 281.1 | 282 | 282 | 282.2 | 281.3 | 280.825 | 282.2 | 271.3 | 281.3 | 281.7 | 272.1 | 281.5 | 281.5 | 281 | 281.7 | 281.8 | 281.2 | 281.8 | 281.6 | 281.9 | 280.7583 | 281.9 | 272.1 | 281.9 | 281 | 281.7 | 281.6 | 282.1 | 272.7 | 281.8 | 281.4 | 271.6 | 281.6 | 281.6 | 281.4 | 280.0333 | 282.1 | 271.6
2026-05-02 | 09:30:00.000 | 281.4 | 281.2 | 281.9 | 282 | 281.4 | 280.9 | 279 | 281 | 281.9 | 281.7 | 281.9 | 280.9 | 281.2667 | 282 | 279 | 281.2 | 271.9 | 279.9 | 281.4 | 281.4 | 281 | 281.5 | 281.6 | 281.1 | 281.6 | 281.4 | 281.6 | 280.4667 | 281.6 | 271.9 | 282 | 280.8 | 281.6 | 281.3 | 281.9 | 281.9 | 281.7 | 281.2 | 281.6 | 271.5 | 271.8 | 280.8 | 279.8417 | 282 | 271.5
2026-05-02 | 09:45:00.000 | 281.6 | 281.3 | 281.9 | 282.1 | 281.5 | 281 | 280.9 | 281.1 | 272.5 | 281.8 | 282 | 280.8 | 280.7083 | 282.1 | 272.5 | 281.2 | 281.6 | 281.5 | 281.4 | 281.4 | 281 | 281.7 | 281.7 | 270.9 | 281.7 | 281.5 | 281.7 | 280.6083 | 281.7 | 270.9 | 282.1 | 280.8 | 281.7 | 281.4 | 282 | 281.9 | 281.7 | 281.3 | 271.8 | 281.5 | 281.6 | 275.8 | 280.3 | 282.1 | 271.8
2026-05-02 | 10:00:00.000 | 281.5 | 281.2 | 281.7 | 272.6 | 281.3 | 280.7 | 280.8 | 280.8 | 271.4 | 281.6 | 281.7 | 280.7 | 279.6667 | 281.7 | 271.4 | 281.2 | 281.5 | 281.3 | 281.3 | 281.3 | 280.9 | 281.5 | 271.4 | 281 | 281.4 | 281.3 | 281.4 | 280.4583 | 281.5 | 271.4 | 281.8 | 280.7 | 281.5 | 281.4 | 281.9 | 281.7 | 281.6 | 281.1 | 281.5 | 281.3 | 281.4 | 275.9 | 280.9833 | 281.9 | 275.9
2026-05-02 | 10:15:00.000 | 281.5 | 281.2 | 281.9 | 282 | 281.5 | 270.7 | 280.9 | 281 | 281.8 | 281.8 | 282 | 280.7 | 280.5833 | 282 | 270.7 | 281.1 | 281.6 | 281.5 | 281.3 | 281.3 | 271.5 | 281.6 | 281.7 | 281.2 | 281.7 | 271.5 | 281.7 | 279.8083 | 281.7 | 271.5 | 282.1 | 280.8 | 271.7 | 281.4 | 281.9 | 281.9 | 281.7 | 281.2 | 281.8 | 281.6 | 281.5 | 280.8 | 280.7 | 282.1 | 271.7
2026-05-02 | 10:30:00.000 | 281.5 | 281.2 | 281.9 | 282.1 | 281.6 | 281 | 280.7 | 280.9 | 281.9 | 281.7 | 281.9 | 280.8 | 281.4333 | 282.1 | 280.7 | 281.2 | 281.6 | 281.5 | 281.4 | 281.4 | 281 | 281.6 | 281.7 | 281.3 | 281.7 | 281.5 | 281.6 | 281.4583 | 281.7 | 281 | 281.4 | 280.8 | 281.8 | 281.3 | 281.9 | 281.8 | 281.6 | 281.3 | 281.7 | 281.6 | 281.5 | 280.7 | 281.45 | 281.9 | 280.7
2026-05-02 | 10:45:00.000 | 280.2 | 279.8 | 279.1 | 280.4 | 278.2 | 278.1 | 278.6 | 278.4 | 279.5 | 280.6 | 278.7 | 278.8 | 279.2 | 280.6 | 278.1 | 278.6 | 278.8 | 279.2 | 278.1 | 278.3 | 278.2 | 280.5 | 279.6 | 279.3 | 270.9 | 280.2 | 280 | 278.475 | 280.5 | 270.9 | 278.6 | 279.1 | 268.9 | 280.2 | 280.5 | 278.5 | 280 | 279.2 | 279.1 | 278.6 | 279.6 | 278.5 | 278.4 | 280.5 | 268.9
2026-05-02 | 11:00:00.000 | 211.5 | 211.5 | 211.5 | 212 | 211.7 | 211.2 | 210.5 | 210.9 | 211.9 | 211.6 | 211.8 | 211 | 211.425 | 212 | 210.5 | 211 | 211.7 | 211.4 | 211.6 | 211.4 | 211 | 211.8 | 211.9 | 211.4 | 204.8 | 211.5 | 211.6 | 210.925 | 211.9 | 204.8 | 211.5 | 210.8 | 211.8 | 211.2 | 211.8 | 204.7 | 211.5 | 211.3 | 211.7 | 211.7 | 211.9 | 210.7 | 210.8833 | 211.9 | 204.7
2026-05-02 | 11:15:00.000 | 90.1 | 90 | 92.3 | 89.6 | 91.3 | 92.3 | 91.8 | 93.1 | 91.3 | 91 | 91.7 | 91.8 | 91.3583 | 93.1 | 89.6 | 92.6 | 91.3 | 92.4 | 90.5 | 91.2 | 91.8 | 92.5 | 92.1 | 91.6 | 91.9 | 89.8 | 90.4 | 91.5083 | 92.6 | 89.8 | 91.2 | 90.4 | 92.3 | 91.2 | 91.1 | 91.9 | 90.6 | 91.8 | 91.7 | 92.8 | 90 | 92.1 | 91.425 | 92.8 | 90
2026-05-02 | 11:30:00.000 | 64.8 | 65.2 | 65.2 | 65.1 | 65.1 | 65.5 | 65.5 | 65.5 | 65.1 | 65.3 | 65.3 | 62.6 | 65.0167 | 65.5 | 62.6 | 63.3 | 65 | 65 | 62.8 | 65.3 | 62.6 | 65.4 | 65.3 | 63 | 65 | 65.1 | 65.4 | 64.4333 | 65.4 | 62.6 | 65.3 | 65.3 | 65.1 | 64.7 | 65 | 62.9 | 65.2 | 64.8 | 65.4 | 65.3 | 65.1 | 65.5 | 64.9667 | 65.5 | 62.9
2026-05-02 | 11:45:00.000 | 62.5 | 65.2 | 65.2 | 65.1 | 65.2 | 65.6 | 62.9 | 65.6 | 65.2 | 65.3 | 65.3 | 64.7 | 64.8167 | 65.6 | 62.5 | 65.5 | 64.9 | 64.9 | 65.1 | 65.2 | 64.8 | 65.3 | 65.3 | 65.2 | 65 | 62.8 | 65.4 | 64.95 | 65.5 | 62.8 | 65.3 | 65.3 | 65.1 | 64.7 | 65 | 65.2 | 63 | 62.4 | 65.4 | 65.3 | 65.1 | 65.6 | 64.7833 | 65.6 | 62.4
2026-05-02 | 12:00:00.000 | 64.9 | 65.2 | 65.2 | 65.2 | 65.2 | 65.6 | 65.5 | 65.5 | 65.1 | 65.4 | 65.3 | 64.7 | 65.2333 | 65.6 | 64.7 | 65.5 | 65 | 65 | 62.7 | 65.3 | 64.8 | 65.3 | 65.3 | 65.2 | 62.8 | 65.1 | 65.3 | 64.775 | 65.5 | 62.7 | 65.3 | 62.9 | 65.1 | 62.5 | 62.6 | 65.2 | 65.3 | 64.8 | 65.4 | 65.3 | 62.9 | 65.5 | 64.4 | 65.5 | 62.5
2026-05-02 | 12:15:00.000 | 64.9 | 65.2 | 65.2 | 65.2 | 65.2 | 65.6 | 65.5 | 65.5 | 65.2 | 65.4 | 65.3 | 64.8 | 65.25 | 65.6 | 64.8 | 65.6 | 65 | 65 | 65.1 | 65.3 | 64.8 | 65.4 | 65.4 | 65.2 | 65 | 65.2 | 65.4 | 65.2 | 65.6 | 64.8 | 65.3 | 65.3 | 62.8 | 64.7 | 62.8 | 65.3 | 58.1 | 64.9 | 65.4 | 65.3 | 65.1 | 65.5 | 64.2083 | 65.5 | 58.1
2026-05-02 | 12:30:00.000 | 64.9 | 65.2 | 65.2 | 65.2 | 65.2 | 65.6 | 65.5 | 65.6 | 65.2 | 65.4 | 65.4 | 64.8 | 65.2667 | 65.6 | 64.8 | 65.6 | 65.1 | 65 | 65.2 | 65.4 | 64.9 | 65.4 | 65.4 | 65.2 | 65.1 | 65.2 | 65.4 | 65.2417 | 65.6 | 64.9 | 65.4 | 65.3 | 65.1 | 64.7 | 63.3 | 65.3 | 65.3 | 64.9 | 65.4 | 65.3 | 65.2 | 65.6 | 65.0667 | 65.6 | 63.3
2026-05-02 | 12:45:00.000 | 65 | 65.3 | 65.2 | 65.3 | 65.3 | 65.6 | 65.6 | 65.6 | 65.2 | 65.5 | 65.4 | 64.9 | 65.325 | 65.6 | 64.9 | 63.4 | 65.1 | 65 | 63 | 65.4 | 64.9 | 65.4 | 65.4 | 65.2 | 62.8 | 65.2 | 65.4 | 64.6833 | 65.4 | 62.8 | 62.9 | 65.4 | 65.1 | 64.7 | 62.1 | 65.3 | 65.4 | 64.9 | 65.5 | 65.3 | 65.2 | 65.6 | 64.7833 | 65.6 | 62.1
2026-05-02 | 13:00:00.000 | 65 | 65.3 | 65.3 | 65.2 | 65.3 | 65.6 | 65.6 | 65.6 | 63 | 65.5 | 65.3 | 65.4 | 65.175 | 65.6 | 63 | 65.6 | 65.1 | 65.1 | 65.3 | 65.3 | 65 | 65.5 | 65.5 | 65.3 | 65.1 | 65.2 | 63.2 | 65.1 | 65.6 | 63.2 | 65.4 | 65.4 | 65.2 | 64.8 | 65.1 | 65.4 | 65.4 | 65 | 65.5 | 64.8 | 65 | 65.6 | 65.2167 | 65.6 | 64.8
2026-05-02 | 13:15:00.000 | 65 | 65.3 | 65.3 | 65.3 | 65.3 | 65.6 | 65.6 | 65.6 | 65.3 | 65.5 | 65.3 | 65.3 | 65.3667 | 65.6 | 65 | 65.6 | 65.1 | 65.1 | 65.3 | 65.3 | 64.9 | 65.4 | 65.4 | 65.3 | 65.1 | 65.3 | 65.4 | 65.2667 | 65.6 | 64.9 | 65.4 | 65.4 | 65.2 | 64.8 | 65.2 | 65.5 | 65.4 | 65 | 65.5 | 64.8 | 65 | 65.2 | 65.2 | 65.5 | 64.8
2026-05-02 | 13:30:00.000 | 64.9 | 65.2 | 65.2 | 65.2 | 65.2 | 64.7 | 65.5 | 65.6 | 65.2 | 65.4 | 65.3 | 65.3 | 65.225 | 65.6 | 64.7 | 65.6 | 65.1 | 65.1 | 65.2 | 65.3 | 64.9 | 65.4 | 65.4 | 65 | 64.7 | 65.2 | 65.4 | 65.1917 | 65.6 | 64.7 | 65.1 | 65.4 | 65.2 | 64.7 | 65.1 | 65.4 | 63.1 | 64.7 | 65.4 | 64.8 | 65 | 64.7 | 64.8833 | 65.4 | 63.1
2026-05-02 | 13:45:00.000 | 65 | 65.3 | 65.3 | 65.3 | 65.3 | 64.7 | 65.6 | 65.6 | 65.3 | 65.5 | 65.3 | 65.3 | 65.2917 | 65.6 | 64.7 | 65.6 | 65.1 | 65.1 | 65.3 | 65.3 | 64.9 | 65.5 | 65.5 | 65.3 | 65.1 | 65.3 | 65.5 | 65.2917 | 65.6 | 64.9 | 65 | 65.4 | 65.2 | 64.8 | 65.2 | 65.5 | 65.4 | 65 | 65.5 | 64.8 | 65 | 62.4 | 64.9333 | 65.5 | 62.4
2026-05-02 | 14:00:00.000 | 65 | 65.3 | 65.3 | 65.2 | 65.3 | 64.7 | 65.6 | 65.6 | 65.3 | 65.4 | 65.3 | 65.4 | 65.2833 | 65.6 | 64.7 | 65.6 | 65.1 | 65.1 | 65.3 | 65.3 | 65 | 65.5 | 65.5 | 65.3 | 65.1 | 65.3 | 65.5 | 65.3 | 65.6 | 65 | 65 | 65.4 | 65.2 | 64.8 | 65.2 | 65.5 | 63 | 65 | 65.5 | 64.8 | 65 | 64.7 | 64.925 | 65.5 | 63
2026-05-02 | 14:15:00.000 | 65.1 | 65.4 | 65.3 | 65.3 | 65.3 | 64.8 | 65.6 | 65.7 | 65.3 | 65.5 | 65.3 | 65.4 | 65.3333 | 65.7 | 64.8 | 65.7 | 62.9 | 65.1 | 63 | 65.4 | 65 | 65.5 | 65.5 | 65.3 | 65.2 | 65.3 | 65.5 | 64.95 | 65.7 | 62.9 | 65.1 | 65.5 | 65.3 | 64.8 | 65.2 | 65.5 | 65.5 | 65 | 65.6 | 64.9 | 65.1 | 64.8 | 65.1917 | 65.6 | 64.8
2026-05-02 | 14:30:00.000 | 65 | 63.1 | 65.2 | 65.2 | 65.2 | 64.7 | 65.6 | 65.6 | 65.2 | 65.5 | 65.3 | 65.3 | 65.075 | 65.6 | 63.1 | 65.6 | 65.1 | 65.1 | 65.3 | 65.3 | 65 | 65.4 | 65.5 | 65.3 | 65.1 | 65.3 | 65.4 | 65.2833 | 65.6 | 65 | 65.1 | 65.4 | 65.3 | 64.8 | 65.2 | 65.5 | 63.1 | 65 | 63.1 | 64.8 | 65 | 64.8 | 64.7583 | 65.5 | 63.1
2026-05-02 | 14:45:00.000 | 66.4 | 66.8 | 67.4 | 67 | 66.4 | 65.5 | 67.5 | 67.8 | 67.4 | 66.7 | 66.2 | 67.2 | 66.8583 | 67.8 | 65.5 | 66.8 | 66.5 | 66.1 | 66.9 | 66.9 | 66.3 | 67.3 | 66.3 | 66.1 | 67.1 | 67.2 | 67.6 | 66.7583 | 67.6 | 66.1 | 67 | 66.7 | 67.4 | 65.6 | 66.1 | 66.2 | 66.5 | 66.5 | 67.3 | 66.8 | 66.4 | 66.4 | 66.575 | 67.4 | 65.6
2026-05-02 | 15:00:00.000 | 132.1 | 132.5 | 131.4 | 132.7 | 132 | 130.9 | 133.1 | 131.7 | 131 | 132.3 | 131.8 | 132.7 | 132.0167 | 133.1 | 130.9 | 132.6 | 132.3 | 131.8 | 132.7 | 132.7 | 128.1 | 131.1 | 132 | 131.7 | 131.5 | 131.3 | 131.5 | 131.6083 | 132.7 | 128.1 | 132.8 | 132.4 | 131.3 | 131.2 | 131.7 | 131.5 | 132 | 132.1 | 132.9 | 127.1 | 131.9 | 131.8 | 131.5583 | 132.9 | 127.1
2026-05-02 | 15:15:00.000 | 246.7 | 245.1 | 247.1 | 245.4 | 247.2 | 246.8 | 245.5 | 246.5 | 246.3 | 247.5 | 247.6 | 245.5 | 246.4333 | 247.6 | 245.1 | 239.1 | 245.8 | 248.1 | 246.6 | 246.4 | 245 | 246.7 | 245.5 | 248.1 | 248.1 | 247.5 | 246.6 | 246.125 | 248.1 | 239.1 | 246.1 | 245.3 | 246.7 | 246.3 | 246.9 | 247 | 247.5 | 245.3 | 244.9 | 246.5 | 245.1 | 245.4 | 246.0833 | 247.5 | 244.9
2026-05-02 | 15:30:00.000 | 281.2 | 281.2 | 281.1 | 281.1 | 281.1 | 281.1 | 280.4 | 280.7 | 281 | 281.3 | 281.1 | 281 | 281.025 | 281.3 | 280.4 | 281 | 281.2 | 280.2 | 281.2 | 281.5 | 280.8 | 281.1 | 281 | 281.1 | 281.8 | 281.1 | 280 | 281 | 281.8 | 280 | 281.1 | 281.1 | 281.3 | 279.7 | 280 | 281.5 | 280 | 281.3 | 279.9 | 281.1 | 281.2 | 281.2 | 280.7833 | 281.5 | 279.7
2026-05-02 | 15:45:00.000 | 281.2 | 281.1 | 281.1 | 281.1 | 281.1 | 281.1 | 280.4 | 280.7 | 281 | 281.3 | 281.1 | 281 | 281.0167 | 281.3 | 280.4 | 281.1 | 281.3 | 280.2 | 281.3 | 281.6 | 280.8 | 281.1 | 281 | 281.1 | 281.7 | 281 | 280 | 281.0167 | 281.7 | 280 | 281.1 | 273.3 | 281.3 | 279.7 | 280 | 281.4 | 280 | 281.3 | 279.9 | 281.1 | 281.2 | 281.2 | 280.125 | 281.4 | 273.3
2026-05-02 | 16:00:00.000 | 281.2 | 281.2 | 281.1 | 281.1 | 281.1 | 281.1 | 280.4 | 280.7 | 281.1 | 281.3 | 281.1 | 281 | 281.0333 | 281.3 | 280.4 | 281.1 | 281.3 | 280.2 | 281.3 | 281.6 | 280.8 | 281.1 | 281 | 281.1 | 272.4 | 281.1 | 280 | 280.25 | 281.6 | 272.4 | 281.1 | 279.2 | 281.3 | 279.7 | 280 | 281.5 | 276 | 281.3 | 270.3 | 281.1 | 281.2 | 281.2 | 279.4917 | 281.5 | 270.3
2026-05-02 | 16:15:00.000 | 281.2 | 281.2 | 281.1 | 281.1 | 281.1 | 281.1 | 280.4 | 280.7 | 281 | 281.3 | 281.1 | 281 | 281.025 | 281.3 | 280.4 | 281 | 281.2 | 280.2 | 281.2 | 281.5 | 280.8 | 281 | 281 | 281.1 | 271.7 | 281.1 | 280 | 280.15 | 281.5 | 271.7 | 281.1 | 281.1 | 281.3 | 279.7 | 280 | 281.5 | 274.4 | 271.3 | 279.9 | 281.1 | 281.2 | 281.2 | 279.4833 | 281.5 | 271.3
2026-05-02 | 16:30:00.000 | 281.2 | 281.2 | 281.1 | 281.1 | 281.1 | 281.1 | 280.4 | 280.7 | 281.1 | 281.3 | 281.1 | 281 | 281.0333 | 281.3 | 280.4 | 281.1 | 281.2 | 280.2 | 281.3 | 281.5 | 280.8 | 281 | 281 | 281.1 | 281.7 | 281.1 | 280 | 281 | 281.7 | 280 | 281.1 | 281.1 | 281.3 | 279.7 | 280 | 281.4 | 280 | 281.3 | 279.9 | 281.1 | 281.2 | 281.2 | 280.775 | 281.4 | 279.7
2026-05-02 | 16:45:00.000 | 281.2 | 281.2 | 281.1 | 281.1 | 281.1 | 281.1 | 280.4 | 280.7 | 281 | 281.3 | 281.1 | 281 | 281.025 | 281.3 | 280.4 | 281.1 | 281.3 | 280.2 | 281.3 | 281.5 | 280.8 | 281.1 | 281 | 281.1 | 281.7 | 281.1 | 280 | 281.0167 | 281.7 | 280 | 281.1 | 281 | 281.3 | 279.7 | 280 | 281.4 | 280 | 281.3 | 279.9 | 281.1 | 281.2 | 281.2 | 280.7667 | 281.4 | 279.7
2026-05-02 | 17:00:00.000 | 281.3 | 281.2 | 281.2 | 281.2 | 281.1 | 281.2 | 280.4 | 280.7 | 281.1 | 281.3 | 281.1 | 281 | 281.0667 | 281.3 | 280.4 | 281.2 | 281.3 | 280.2 | 281.4 | 281.6 | 280.8 | 281.1 | 281.1 | 281.1 | 281.8 | 281.1 | 280 | 281.0583 | 281.8 | 280 | 281.1 | 281.1 | 281.3 | 279.7 | 280.1 | 281.5 | 280.1 | 281.4 | 280 | 281.1 | 281.3 | 281.3 | 280.8333 | 281.5 | 279.7
2026-05-02 | 17:15:00.000 | 280.5 | 280.1 | 280.3 | 280.2 | 280.1 | 280.3 | 280.7 | 280.9 | 281.3 | 281.6 | 281.5 | 280.1 | 280.6333 | 281.6 | 280.1 | 270.2 | 279.4 | 277.2 | 269.7 | 273.5 | 281 | 276.6 | 280.2 | 280.3 | 275.2 | 279.9 | 279.2 | 276.8667 | 281 | 269.7 | 281.3 | 281.4 | 261.1 | 279.9 | 280.2 | 281.7 | 280.2 | 261.6 | 280.1 | 281.3 | 281.5 | 280.7 | 277.5833 | 281.7 | 261.1
2026-05-02 | 17:30:00.000 | 258.7 | 248.7 | 257.2 | 258 | 257.9 | 257.5 | 262 | 277.1 | 275.2 | 272.4 | 271.5 | 256.8 | 262.75 | 277.1 | 248.7 | 242.2 | 255.6 | 251.6 | 241 | 245.1 | 252.9 | 249.1 | 254.5 | 257.6 | 246.3 | 255 | 256.4 | 250.6083 | 257.6 | 241 | 279.9 | 280.2 | 269.6 | 278.6 | 276.9 | 278 | 279 | 275.7 | 277.6 | 280.1 | 279.7 | 259.9 | 276.2667 | 280.2 | 259.9
2026-05-02 | 17:45:00.000 | 228.4 | 226.9 | 226.5 | 227.7 | 227.6 | 226.5 | 224.3 | 249.3 | 245.8 | 241.7 | 241 | 226.1 | 232.65 | 249.3 | 224.3 | 213.2 | 225.4 | 222 | 211.6 | 215.3 | 229.2 | 218.9 | 223.8 | 225.8 | 215.5 | 222.3 | 224.2 | 220.6 | 229.2 | 211.6 | 256 | 257 | 253.5 | 253 | 248.3 | 249.6 | 245 | 247.2 | 252.3 | 258 | 255 | 230.4 | 250.4417 | 258 | 230.4
2026-05-02 | 18:00:00.000 | 189.5 | 188.3 | 193.5 | 194.5 | 194.7 | 192.8 | 183.5 | 216 | 212.2 | 208.8 | 209 | 193.9 | 198.0583 | 216 | 183.5 | 182.8 | 192.9 | 190.1 | 180.3 | 183.6 | 195.2 | 186.7 | 191.4 | 192.3 | 183.4 | 188.6 | 190.6 | 188.1583 | 195.2 | 180.3 | 222.4 | 224.6 | 218.9 | 215.5 | 213 | 214.2 | 219.6 | 213.1 | 210.9 | 225.4 | 219.9 | 198.3 | 216.3167 | 225.4 | 198.3
2026-05-02 | 18:15:00.000 | 160.8 | 160.1 | 159.1 | 160.2 | 160.3 | 157.8 | 149.1 | 178.7 | 175.2 | 172.3 | 172.1 | 160.1 | 163.8167 | 178.7 | 149.1 | 145.2 | 157.4 | 157.1 | 148 | 149.5 | 159.3 | 147.2 | 156.7 | 156.5 | 148.2 | 151.1 | 153.3 | 152.4583 | 159.3 | 145.2 | 185.6 | 188.5 | 181.6 | 176.4 | 176 | 178.9 | 183.8 | 178.5 | 183.9 | 189.8 | 181.6 | 159.7 | 180.3583 | 189.8 | 159.7
2026-05-02 | 18:30:00.000 | 127.8 | 127.3 | 126.3 | 127.3 | 127.5 | 123.9 | 116.3 | 143.9 | 140.5 | 137.9 | 137.9 | 126.1 | 130.225 | 143.9 | 116.3 | 118.9 | 124.1 | 124.2 | 115.9 | 116.4 | 123.8 | 115.5 | 122.5 | 121.8 | 114.8 | 115.8 | 118.2 | 119.325 | 124.2 | 114.8 | 149.8 | 151.6 | 142.9 | 139.1 | 138.4 | 142.5 | 147.4 | 143.2 | 148.5 | 153.9 | 146.4 | 133.1 | 144.7333 | 153.9 | 133.1
2026-05-02 | 18:45:00.000 | 93.7 | 93.3 | 89.6 | 93.5 | 93.7 | 89.5 | 84.4 | 107.7 | 105.3 | 102.5 | 102.5 | 92.3 | 95.6667 | 107.7 | 84.4 | 86.6 | 90.6 | 90.1 | 82.9 | 83.9 | 88.8 | 86.1 | 88.2 | 87.1 | 81.6 | 81 | 83.2 | 85.8417 | 90.6 | 81 | 112.5 | 113.2 | 102.3 | 103.3 | 98.6 | 105.3 | 106 | 106.5 | 111.9 | 116.1 | 108.1 | 96.1 | 106.6583 | 116.1 | 96.1
2026-05-02 | 19:00:00.000 | 61.9 | 61.2 | 60.5 | 61.7 | 61.9 | 58.1 | 56.3 | 73.4 | 71.6 | 67 | 69 | 61.5 | 63.675 | 73.4 | 56.3 | 56.5 | 59.8 | 58.6 | 53 | 53.9 | 56.6 | 54.8 | 56.6 | 55.5 | 51.6 | 50 | 52.1 | 54.9167 | 59.8 | 50 | 76.5 | 77.4 | 71 | 70 | 66.6 | 70.5 | 74.5 | 66.7 | 77.1 | 80.5 | 72.4 | 68.3 | 72.625 | 80.5 | 66.6
2026-05-02 | 19:15:00.000 | 34.4 | 33.8 | 33.3 | 34.3 | 34.5 | 32 | 33 | 43.3 | 42.1 | 40.3 | 40 | 34.8 | 36.3167 | 43.3 | 32 | 30.6 | 32.9 | 31.8 | 27.7 | 28.7 | 29.7 | 28.8 | 29.7 | 28.4 | 25.8 | 23.9 | 26.2 | 28.6833 | 32.9 | 23.9 | 45.2 | 46.4 | 40.9 | 41.3 | 40.6 | 39.9 | 43.6 | 42.1 | 46.3 | 49.3 | 41.3 | 40.6 | 43.125 | 49.3 | 39.9
2026-05-02 | 19:30:00.000 | 14.3 | 14.1 | 14 | 14.4 | 13.9 | 13 | 14.9 | 19.7 | 19.1 | 18.1 | 17.9 | 15.3 | 15.725 | 19.7 | 13 | 12.1 | 13.4 | 12.8 | 10.5 | 11.9 | 12.7 | 13 | 14.1 | 14.2 | 13.8 | 14 | 15.2 | 13.1417 | 15.2 | 10.5 | 20.7 | 21.9 | 19.4 | 18.7 | 18.5 | 16.6 | 18.9 | 18.3 | 21.2 | 23.8 | 18.4 | 18.1 | 19.5417 | 23.8 | 16.6
2026-05-02 | 19:45:00.000 | 6.5 | 6.3 | 6.2 | 6 | 6.5 | 6.1 | 5.5 | 6.8 | 6.7 | 6.3 | 5.9 | 5.6 | 6.2 | 6.8 | 5.5 | 6.3 | 5.9 | 5.9 | 6.1 | 6.7 | 6.6 | 7 | 7.3 | 8.2 | 8.2 | 8.3 | 8.3 | 7.0667 | 8.3 | 5.9 | 7 | 7 | 6.7 | 6.2 | 6.4 | 5.8 | 6.3 | 6.3 | 7.1 | 7.9 | 6.5 | 6.3 | 6.625 | 7.9 | 5.8
2026-05-02 | 20:00:00.000 | 1.9 | 1.8 | 1.9 | 2 | 2 | 2.2 | 2 | 2.1 | 2.2 | 2.2 | 2.1 | 1.9 | 2.025 | 2.2 | 1.8 | 1.8 | 1.9 | 1.8 | 1.8 | 1.8 | 2 | 2 | 2.1 | 2.2 | 2 | 2.2 | 2.2 | 1.9833 | 2.2 | 1.8 | 2.1 | 1.8 | 2.1 | 2 | 2.2 | 2 | 2 | 2.1 | 2.2 | 2.2 | 2.1 | 1.8 | 2.05 | 2.2 | 1.8
2026-05-02 | 20:15:00.000 | 0.3 | 0.2 | 0.5 | 0.5 | 0.7 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.48333 | 0.7 | 0.2 | 0.5 | 0.5 | 0.2 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.4 | 0.5 | 0.50833 | 0.6 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.58333 | 0.6 | 0.5
2026-05-02 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.125 | 0.3 | 0.1 | 0.1 | 0.1 | 0.8 | 0.1 | 0.4 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.4 | 0.21667 | 0.8 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11667 | 0.3 | 0.1
2026-05-02 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.11667 | 0.2 | 0 | 0.2 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0.12 | 0.2 | 0
2026-05-02 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0
2026-05-02 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-02 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320