## PR_Calc
PR CALCULATION
03 MAGGIO 2026 | [67 empty] | 3 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 52
RAW PR | [64 empty] | 0.85254 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 85.2536
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 85.2871
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 71.2646
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-03 | 00:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8330.9
2026-05-03 | 00:15:00.000 | -1.9 | -0.000475 | -1.6 | -0.0004 | -0.0004375 | 0 | -0.0004375 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 00:30:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 00:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 01:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 01:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 01:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 01:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 02:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 02:15:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 02:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 02:45:00.000 | -0.9 | -0.000225 | -0.8 | -0.0002 | -0.0002125 | 0 | -0.0002125 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 03:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 03:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 03:30:00.000 | -0.5 | -0.000125 | -0.8 | -0.0002 | -0.0001625 | 0 | -0.0001625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 03:45:00.000 | -0.8 | -0.0002 | -0.2 | -5e-05 | -0.000125 | 0 | -0.000125 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 04:00:00.000 | -0.5 | -0.000125 | -0.1 | -2.5e-05 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 04:15:00.000 | -0.4 | -0.0001 | -0.2 | -5e-05 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 04:30:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 04:45:00.000 | -1 | -0.00025 | -0.3 | -7.5e-05 | -0.0001625 | 0 | -0.0001625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 05:00:00.000 | -1 | -0.00025 | -1.1 | -0.000275 | -0.0002625 | 0 | -0.0002625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 05:15:00.000 | -1 | -0.00025 | -1.6 | -0.0004 | -0.000325 | 0 | -0.000325 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 05:30:00.000 | -1 | -0.00025 | -1.9 | -0.000475 | -0.0003625 | 0 | -0.0003625 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 05:45:00.000 | -1 | -0.00025 | -1.4 | -0.00035 | -0.0003 | 0 | -0.0003 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 06:00:00.000 | -0.4 | -0.0001 | -0.5 | -0.000125 | -0.0001125 | 0 | -0.0001125 | 0 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 06:15:00.000 | 2.5 | 0.000625 | 2 | 0.0005 | 0.0005625 | 0 | 0.0005625 | 0.22222 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 06:30:00.000 | 17.6 | 0.0044 | 14.8 | 0.0037 | 0.00405 | 0 | 0.00405 | 0.17284 | 30215.7 | 30215.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 06:45:00.000 | 54.6 | 0.01365 | 52.9 | 0.013225 | 0.013437 | 53.75 | 0.01365 | 0.031628 | 30215.7 | 30215.8 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 07:00:00.000 | 112.8 | 0.0282 | 110.5 | 0.027625 | 0.027912 | 111.65 | 0.0282 | 0.0206 | 30215.8 | 30216 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 07:15:00.000 | 201.4 | 0.05035 | 168.3 | 0.042075 | 0.046213 | 184.85 | 0.05035 | 0.17906 | 30216 | 30216.3 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 07:30:00.000 | 294.6 | 0.07365 | 270 | 0.0675 | 0.070575 | 282.3 | 0.07365 | 0.087141 | 30216.3 | 30216.9 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 07:45:00.000 | 362.2 | 0.09055 | 387.2 | 0.0968 | 0.093675 | 374.7 | 0.0968 | 0.06672 | 30216.9 | 30217.8 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 08:00:00.000 | 451.9 | 0.11297 | 445.4 | 0.11135 | 0.11216 | 448.65 | 0.11297 | 0.014488 | 30217.8 | 30218.9 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 08:15:00.000 | 566.2 | 0.14155 | 563.4 | 0.14085 | 0.1412 | 564.8 | 0.14155 | 0.0049575 | 30218.9 | 30220.4 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 08:30:00.000 | 649 | 0.16225 | 659.5 | 0.16487 | 0.16356 | 654.25 | 0.16487 | 0.016049 | 30220.4 | 30222.2 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 08:45:00.000 | 736.7 | 0.18418 | 734.4 | 0.1836 | 0.18389 | 735.55 | 0.18418 | 0.0031269 | 30222.2 | 30224.1 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 09:00:00.000 | 838.1 | 0.20953 | 834.9 | 0.20872 | 0.20913 | 836.5 | 0.20953 | 0.0038255 | 30224.1 | 30226.4 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 09:15:00.000 | 753.8 | 0.18845 | 748.4 | 0.1871 | 0.18777 | 751.1 | 0.18845 | 0.0071895 | 30226.4 | 30228.8 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 09:30:00.000 | 806.1 | 0.20153 | 797.4 | 0.19935 | 0.20044 | 801.75 | 0.20153 | 0.010851 | 30228.8 | 30230.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 09:45:00.000 | 858.1 | 0.21452 | 856.1 | 0.21402 | 0.21427 | 857.1 | 0.21452 | 0.0023335 | 30230.9 | 30233.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 10:00:00.000 | 574.6 | 0.14365 | 593.6 | 0.1484 | 0.14603 | 584.1 | 0.1484 | 0.032529 | 30233.2 | 30234.9 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 10:15:00.000 | 674 | 0.1685 | 634.1 | 0.15852 | 0.16351 | 654.05 | 0.1685 | 0.061005 | 30234.9 | 30236.6 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 10:30:00.000 | 591.3 | 0.14782 | 566.6 | 0.14165 | 0.14474 | 578.95 | 0.14782 | 0.042663 | 30236.6 | 30238.4 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 10:45:00.000 | 831.9 | 0.20797 | 812 | 0.203 | 0.20549 | 821.95 | 0.20797 | 0.024211 | 30238.4 | 30239.8 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 11:00:00.000 | 783 | 0.19575 | 745.6 | 0.1864 | 0.19107 | 764.3 | 0.19575 | 0.048934 | 30239.8 | 30241.6 | 1800 | 0.6117 | 9.9808 | 9.9808 | 9.9808 | 9.9808 | 9.9808 | 9.9808 | 9.9808 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 9.9808 | 10.8735 | 12.6588 | 9.9808 | 130.4815 | 7.3027 | 9.9808 | 9.9808 | 7.3027 | 7.3027 | 12.6588 | 9.9808 | 12.6588 | 12.6588 | 9.9808 | 12.6588 | 12.6588 | 10.4271 | 12.6588 | 7.3027 | 125.1255 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 12.6588 | 7.3027 | 12.1719 | 12.6588 | 7.3027 | 146.5497 | 0.83019
2026-05-03 | 11:15:00.000 | 937.3 | 0.23432 | 910.9 | 0.22772 | 0.23102 | 924.1 | 0.23432 | 0.028568 | 30241.6 | 30242.7 | 1100 | 0.3282 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 41.7412 | 43.824 | 43.824 | 41.7412 | 41.7412 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.3033 | 43.824 | 41.7412 | 519.6395 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 41.7412 | 43.6347 | 43.824 | 41.7412 | 523.8052 | 0.83019
2026-05-03 | 11:30:00.000 | 875.7 | 0.21893 | 850.4 | 0.2126 | 0.21576 | 863.05 | 0.21893 | 0.029315 | 30242.7 | 30243.6 | 900 | 0.3282 | 40.273 | 40.273 | 40.273 | 40.273 | 40.273 | 40.273 | 40.273 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 40.273 | 41.281 | 43.2971 | 40.273 | 495.3724 | 37.249 | 40.273 | 40.273 | 37.249 | 37.249 | 43.2971 | 40.273 | 43.2971 | 43.2971 | 40.273 | 43.2971 | 43.2971 | 40.777 | 43.2971 | 37.249 | 489.3243 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 43.2971 | 37.249 | 42.7472 | 43.2971 | 37.249 | 513.5167 | 0.83019
2026-05-03 | 11:45:00.000 | 888.9 | 0.22223 | 878.2 | 0.21955 | 0.22089 | 883.55 | 0.22223 | 0.01211 | 30243.6 | 30244.5 | 900 | 0.3282 | 41.8533 | 41.8533 | 41.8533 | 41.8533 | 41.8533 | 41.8533 | 41.8533 | 43.824 | 43.824 | 43.824 | 43.824 | 41.8533 | 42.5102 | 43.824 | 41.8533 | 510.1222 | 38.7574 | 41.8533 | 41.8533 | 38.7574 | 38.7574 | 43.824 | 41.8533 | 43.824 | 43.824 | 41.8533 | 43.824 | 43.824 | 41.9004 | 43.824 | 38.7574 | 502.8053 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 38.7574 | 43.3634 | 43.824 | 38.7574 | 520.8214 | 0.83019
2026-05-03 | 12:00:00.000 | 620.6 | 0.15515 | 704.9 | 0.17622 | 0.16569 | 662.75 | 0.17622 | 0.1272 | 30244.5 | 30245.5 | 1000 | 0.3282 | 24.8327 | 24.8327 | 24.8327 | 24.8327 | 24.8327 | 24.8327 | 24.8327 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 24.8327 | 25.6068 | 27.1549 | 24.8327 | 307.2813 | 22.5105 | 24.8327 | 24.8327 | 22.5105 | 22.5105 | 27.1549 | 24.8327 | 27.1549 | 27.1549 | 24.8327 | 27.1549 | 27.1549 | 25.2197 | 27.1549 | 22.5105 | 302.6369 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 27.1549 | 22.5105 | 26.7327 | 27.1549 | 22.5105 | 321.2146 | 0.83019
2026-05-03 | 12:15:00.000 | 756.5 | 0.18912 | 678.7 | 0.16968 | 0.1794 | 717.6 | 0.18912 | 0.10842 | 30245.5 | 30246.4 | 900 | 0.3282 | 29.0609 | 29.0609 | 29.0609 | 29.0609 | 29.0609 | 29.0609 | 29.0609 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 29.0609 | 29.899 | 31.5753 | 29.0609 | 358.788 | 26.5465 | 29.0609 | 29.0609 | 26.5465 | 26.5465 | 31.5753 | 29.0609 | 31.5753 | 31.5753 | 29.0609 | 31.5753 | 31.5753 | 29.4799 | 31.5753 | 26.5465 | 353.7592 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 31.5753 | 26.5465 | 31.1181 | 31.5753 | 26.5465 | 373.8745 | 0.83019
2026-05-03 | 12:30:00.000 | 937.1 | 0.23428 | 913.3 | 0.22833 | 0.2313 | 925.2 | 0.23428 | 0.025724 | 30246.4 | 30247.4 | 1000 | 0.3282 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 41.8221 | 43.824 | 43.824 | 41.8221 | 41.8221 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.3235 | 43.824 | 41.8221 | 519.8823 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 41.8221 | 43.642 | 43.824 | 41.8221 | 523.8861 | 0.83019
2026-05-03 | 12:45:00.000 | 873.7 | 0.21843 | 837.5 | 0.20938 | 0.2139 | 855.6 | 0.21843 | 0.042309 | 30247.4 | 30248.3 | 900 | 0.3282 | 39.6987 | 39.6987 | 39.6987 | 39.6987 | 39.6987 | 39.6987 | 39.6987 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 39.6987 | 40.698 | 42.6967 | 39.6987 | 488.3765 | 36.7008 | 39.6987 | 39.6987 | 36.7008 | 36.7008 | 42.6967 | 39.6987 | 42.6967 | 42.6967 | 39.6987 | 42.6967 | 42.6967 | 40.1984 | 42.6967 | 36.7008 | 482.3806 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 42.6967 | 36.7008 | 42.1516 | 42.6967 | 36.7008 | 506.3642 | 0.83019
2026-05-03 | 13:00:00.000 | 984.5 | 0.24613 | 954.3 | 0.23857 | 0.24235 | 969.4 | 0.24613 | 0.031153 | 30248.3 | 30249.3 | 1000 | 0.3282 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 0.83019
2026-05-03 | 13:15:00.000 | 974.1 | 0.24353 | 937.2 | 0.2343 | 0.23891 | 955.65 | 0.24353 | 0.038612 | 30249.3 | 30250.2 | 900 | 0.3282 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 0.83019
2026-05-03 | 13:30:00.000 | 1042.5 | 0.26062 | 1013.7 | 0.25343 | 0.25703 | 1028.1 | 0.26062 | 0.028013 | 30250.2 | 30251.2 | 1000 | 0.3282 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 43.824 | 525.888 | 0.83019
2026-05-03 | 13:45:00.000 | 809.9 | 0.20247 | 792.5 | 0.19812 | 0.2003 | 801.2 | 0.20247 | 0.021717 | 30251.2 | 30252.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 14:00:00.000 | 827.5 | 0.20688 | 807.6 | 0.2019 | 0.20439 | 817.55 | 0.20688 | 0.024341 | 30252.7 | 30254.8 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 14:15:00.000 | 1012.6 | 0.25315 | 990.4 | 0.2476 | 0.25038 | 1001.5 | 0.25315 | 0.022167 | 30254.8 | 30257.2 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 14:30:00.000 | 996.4 | 0.2491 | 973.4 | 0.24335 | 0.24622 | 984.9 | 0.2491 | 0.023353 | 30257.2 | 30259.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 14:45:00.000 | 955.6 | 0.2389 | 931.8 | 0.23295 | 0.23592 | 943.7 | 0.2389 | 0.02522 | 30259.7 | 30262.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 15:00:00.000 | 959.7 | 0.23992 | 937.4 | 0.23435 | 0.23714 | 948.55 | 0.23992 | 0.02351 | 30262.2 | 30264.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 15:15:00.000 | 987.6 | 0.2469 | 961.2 | 0.2403 | 0.2436 | 974.4 | 0.2469 | 0.027094 | 30264.6 | 30267.1 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 15:30:00.000 | 1013.5 | 0.25338 | 989.4 | 0.24735 | 0.25036 | 1001.45 | 0.25338 | 0.024065 | 30267.1 | 30269.6 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 15:45:00.000 | 1017 | 0.25425 | 993.1 | 0.24827 | 0.25126 | 1005.05 | 0.25425 | 0.02378 | 30269.6 | 30272 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 16:00:00.000 | 945.1 | 0.23628 | 916.6 | 0.22915 | 0.23271 | 930.85 | 0.23628 | 0.030617 | 30272 | 30274.5 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 16:15:00.000 | 903.3 | 0.22582 | 883.2 | 0.2208 | 0.22331 | 893.25 | 0.22582 | 0.022502 | 30274.5 | 30276.8 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 16:30:00.000 | 838.8 | 0.2097 | 809.7 | 0.20243 | 0.20606 | 824.25 | 0.2097 | 0.035305 | 30276.8 | 30279.2 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 16:45:00.000 | 504.4 | 0.1261 | 483.6 | 0.1209 | 0.1235 | 494 | 0.1261 | 0.042105 | 30279.2 | 30281 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 17:00:00.000 | 582.7 | 0.14567 | 564.8 | 0.1412 | 0.14344 | 573.75 | 0.14567 | 0.031198 | 30281 | 30282.3 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 17:15:00.000 | 487 | 0.12175 | 480.8 | 0.1202 | 0.12097 | 483.9 | 0.12175 | 0.012813 | 30282.3 | 30283.9 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 17:30:00.000 | 324.5 | 0.081125 | 327.1 | 0.081775 | 0.08145 | 325.8 | 0.081775 | 0.0079804 | 30283.9 | 30284.9 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 17:45:00.000 | 264.7 | 0.066175 | 266 | 0.0665 | 0.066337 | 265.35 | 0.0665 | 0.0048992 | 30284.9 | 30285.9 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 18:00:00.000 | 237.7 | 0.059425 | 245.4 | 0.06135 | 0.060387 | 241.55 | 0.06135 | 0.031877 | 30285.9 | 30286.6 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 18:15:00.000 | 266 | 0.0665 | 284.2 | 0.07105 | 0.068775 | 275.1 | 0.07105 | 0.066158 | 30286.6 | 30287.3 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 18:30:00.000 | 333.2 | 0.0833 | 370.6 | 0.09265 | 0.087975 | 351.9 | 0.09265 | 0.10628 | 30287.3 | 30288.3 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 18:45:00.000 | 146.4 | 0.0366 | 159.4 | 0.03985 | 0.038225 | 152.9 | 0.03985 | 0.085023 | 30288.3 | 30289 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 19:00:00.000 | 102.7 | 0.025675 | 108.7 | 0.027175 | 0.026425 | 105.7 | 0.027175 | 0.056764 | 30289 | 30289.4 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 19:15:00.000 | 160.5 | 0.040125 | 204.6 | 0.05115 | 0.045637 | 182.55 | 0.05115 | 0.24158 | 30289.4 | 30289.8 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 19:30:00.000 | 83.5 | 0.020875 | 110.9 | 0.027725 | 0.0243 | 97.2 | 0.027725 | 0.28189 | 30289.8 | 30290.2 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 19:45:00.000 | 21.9 | 0.005475 | 22.7 | 0.005675 | 0.005575 | 0 | 0.005575 | 0.035874 | 30290.2 | 30290.3 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 20:00:00.000 | 3.5 | 0.000875 | 3.3 | 0.000825 | 0.00085 | 0 | 0.00085 | 0.058824 | 30290.3 | 30290.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 20:15:00.000 | -1.7 | -0.000425 | -2 | -0.0005 | -0.0004625 | 0 | -0.0004625 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 20:30:00.000 | -2.9 | -0.000725 | -3 | -0.00075 | -0.0007375 | 0 | -0.0007375 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 20:45:00.000 | -2.8 | -0.0007 | -2.2 | -0.00055 | -0.000625 | 0 | -0.000625 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 21:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 21:15:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 21:30:00.000 | -1.6 | -0.0004 | -2 | -0.0005 | -0.00045 | 0 | -0.00045 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 21:45:00.000 | -2 | -0.0005 | -1.4 | -0.00035 | -0.000425 | 0 | -0.000425 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 22:00:00.000 | -2 | -0.0005 | -1.7 | -0.000425 | -0.0004625 | 0 | -0.0004625 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 22:15:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 22:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 22:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 23:00:00.000 | -0.9 | -0.000225 | -0.5 | -0.000125 | -0.000175 | 0 | -0.000175 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 23:15:00.000 | -0.2 | -5e-05 | -0.3 | -7.5e-05 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
2026-05-03 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83019
PR for each inverter |  |  | 8.4478 |  | 8.3127 | 8.3803 |  | 8.5219 |  |  |  | 74700 |  | 0.8635 | 0.85919 | 0.86139 | 0.86513 | 0.86054 | 0.86104 | 0.8618 | 0.84872 | 0.84445 | 0.84258 | 0.84151 | 0.86669 | #DIV/0! | #DIV/0! | #DIV/0! | 4919.862 | 0.87505 | 0.85552 | 0.85507 | 0.87238 | 0.87651 | 0.84106 | 0.85586 | 0.83549 | 0.83636 | 0.8532 | 0.83387 | 0.83514 |  |  |  | 4873.2176 | 0.84974 | 0.8445 | 0.84419 | 0.85184 | 0.84483 | 0.84818 | 0.85027 | 0.84249 | 0.8465 | 0.84582 | 0.85235 | 0.88063 | #DIV/0! | #DIV/0! | #DIV/0! | 5007.6963 |  | 0.85287 |  | #DIV/0! | #DIV/0! | 7.7475e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-03 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 06:30:00.000 | 0.5 | 0 | 0.4 | 0.4 | 2.3 | 1.6 | 0.6 | 0 | 1 | 0.1 | 0.5 | 1.1 | 0.85 | 2.3 | 0 | 0.7 | 0.4 | 2.5 | 1.5 | 1.8 | 0.8 | 1.1 | 3.5 | 1 | 0.7 | 0.5 | 3 | 1.4583 | 3.5 | 0.4 | 2 | 0 | 0 | 0 | 0.5 | 0.9 | 0.3 | 0.2 | 0 | 0 | 0.3 | 0.9 | 0.72857 | 2 | 0
2026-05-03 | 06:45:00.000 | 8.6 | 8.2 | 9.7 | 9.8 | 9.6 | 9.9 | 9.5 | 8.7 | 9.7 | 9.1 | 9.6 | 10.1 | 9.375 | 10.1 | 8.2 | 9.2 | 8.8 | 9.5 | 9.9 | 9.6 | 9.9 | 10.1 | 10.9 | 10.9 | 9.8 | 10.1 | 10.6 | 9.9417 | 10.9 | 8.8 | 10 | 7.6 | 8.7 | 9.9 | 9.9 | 11 | 10.5 | 10.3 | 9.7 | 8.3 | 10.3 | 9.8 | 9.6667 | 11 | 7.6
2026-05-03 | 07:00:00.000 | 24 | 23.9 | 25.8 | 25.6 | 25.9 | 24.8 | 24.5 | 23.7 | 25.1 | 25.3 | 26.3 | 25.8 | 25.0583 | 26.3 | 23.7 | 23.3 | 22.3 | 23.8 | 25.1 | 24.6 | 25.1 | 25.8 | 26.8 | 28 | 25.9 | 27.8 | 27.5 | 25.5 | 28 | 22.3 | 27.8 | 23.8 | 25.8 | 27.5 | 27.4 | 30.1 | 29 | 28.4 | 27 | 24.6 | 27.2 | 27 | 27.1333 | 30.1 | 23.8
2026-05-03 | 07:15:00.000 | 49.1 | 48.9 | 51.7 | 50.6 | 51 | 49.3 | 48.3 | 49.6 | 50.7 | 50.6 | 52.5 | 51.2 | 50.2917 | 52.5 | 48.3 | 46.2 | 45 | 47.2 | 49 | 48.5 | 50.7 | 50.6 | 52.3 | 54.4 | 50.8 | 54.3 | 53.3 | 50.1917 | 54.4 | 45 | 54.5 | 49.1 | 52.1 | 54.9 | 54.7 | 57.7 | 55.9 | 55.3 | 53.5 | 50.5 | 55.7 | 51.9 | 53.8167 | 57.7 | 49.1
2026-05-03 | 07:30:00.000 | 80 | 79.6 | 82.3 | 78.1 | 81.3 | 79.7 | 78.3 | 82 | 82.5 | 82.3 | 84.3 | 82.4 | 81.0667 | 84.3 | 78.1 | 75.2 | 74.6 | 76.7 | 77.9 | 77.4 | 82 | 81 | 83.6 | 85.9 | 80.9 | 86 | 84.2 | 80.45 | 86 | 74.6 | 87.1 | 81.3 | 84.6 | 87.8 | 87 | 90.3 | 88.2 | 87.1 | 85.3 | 82 | 88.2 | 82.1 | 85.9167 | 90.3 | 81.3
2026-05-03 | 07:45:00.000 | 109 | 108.4 | 110.9 | 110.1 | 110.3 | 108.4 | 107.3 | 112.8 | 112.6 | 111.9 | 114.1 | 111.4 | 110.6 | 114.1 | 107.3 | 103.2 | 104.1 | 105.5 | 105.4 | 105.2 | 113 | 110.1 | 113.2 | 115.1 | 109.1 | 115.7 | 113 | 109.3833 | 115.7 | 103.2 | 116.8 | 110.8 | 114.4 | 117.4 | 112.3 | 119.8 | 117.7 | 116.4 | 114.9 | 111.3 | 118.5 | 109.3 | 114.9667 | 119.8 | 109.3
2026-05-03 | 08:00:00.000 | 139.3 | 138.2 | 140.9 | 139.9 | 139.8 | 137.8 | 136.6 | 145.5 | 144.1 | 143 | 145 | 141.1 | 140.9333 | 145.5 | 136.6 | 131.2 | 133.6 | 134.6 | 133.1 | 133.2 | 144.8 | 139.9 | 144.2 | 145.5 | 138.4 | 145.7 | 143 | 138.9333 | 145.7 | 131.2 | 148 | 143.6 | 147 | 150.4 | 149.9 | 152.4 | 151.4 | 148.2 | 146.8 | 144.1 | 150.9 | 138 | 147.5583 | 152.4 | 138
2026-05-03 | 08:15:00.000 | 173.3 | 176.8 | 178.7 | 179.2 | 179 | 177.5 | 177.2 | 187.2 | 185 | 184 | 185.2 | 180.9 | 180.3333 | 187.2 | 173.3 | 170 | 168.3 | 174.9 | 171.7 | 172.4 | 186.4 | 179.4 | 184.9 | 185.8 | 177.5 | 186.5 | 183.5 | 178.4417 | 186.5 | 168.3 | 183.5 | 179.2 | 189 | 191.9 | 191.3 | 193.2 | 193.2 | 177.3 | 183.5 | 186 | 192.2 | 174.7 | 186.25 | 193.2 | 174.7
2026-05-03 | 08:30:00.000 | 208 | 199.3 | 208.9 | 209.1 | 208.7 | 207.4 | 207.5 | 219.6 | 216.2 | 214.8 | 216.1 | 210.7 | 210.525 | 219.6 | 199.3 | 198 | 203.5 | 204.6 | 199.1 | 199.9 | 210.8 | 208.2 | 215.6 | 215.7 | 206.1 | 215.6 | 212.2 | 207.4417 | 215.7 | 198 | 220.1 | 217.8 | 220.9 | 223.9 | 223.6 | 224.9 | 225.9 | 220.4 | 220.3 | 217.8 | 223.6 | 204.8 | 220.3333 | 225.9 | 204.8
2026-05-03 | 08:45:00.000 | 231.2 | 229.3 | 231.5 | 232.8 | 232 | 230.7 | 232.2 | 244 | 240.6 | 239 | 239.7 | 225.9 | 234.075 | 244 | 225.9 | 220.4 | 228.7 | 228.1 | 221.8 | 223 | 243 | 222.8 | 239.3 | 238.9 | 228.5 | 239.3 | 236 | 230.8167 | 243 | 220.4 | 244.4 | 243.4 | 245.5 | 248.5 | 248 | 248 | 250.1 | 243.2 | 243.9 | 242.5 | 247.5 | 226.2 | 244.2667 | 250.1 | 226.2
2026-05-03 | 09:00:00.000 | 264.8 | 262.3 | 266.6 | 267.2 | 258.1 | 266.5 | 269.1 | 278.9 | 276 | 274.5 | 275.4 | 269.1 | 269.0417 | 278.9 | 258.1 | 254.7 | 265.8 | 264 | 255.7 | 257.6 | 277.1 | 265.6 | 274 | 263.5 | 262.7 | 274.3 | 264.4 | 264.95 | 277.1 | 254.7 | 276.8 | 277.1 | 277.7 | 279.1 | 248 | 277.9 | 269.2 | 274.8 | 276.3 | 276.1 | 278.5 | 256.7 | 272.35 | 279.1 | 248
2026-05-03 | 09:15:00.000 | 244.5 | 241.7 | 242.9 | 244.4 | 241.5 | 241.8 | 243.2 | 254.9 | 250.7 | 247.5 | 246.4 | 242 | 245.125 | 254.9 | 241.5 | 229.7 | 239.2 | 240.1 | 214.3 | 231.8 | 239.6 | 234.4 | 247 | 245.7 | 236.7 | 245.5 | 242.5 | 237.2083 | 247 | 214.3 | 251.8 | 242.9 | 251.9 | 252.8 | 253.9 | 252.6 | 256.5 | 250.1 | 250.4 | 251.2 | 254.2 | 235 | 250.275 | 256.5 | 235
2026-05-03 | 09:30:00.000 | 253.1 | 250.9 | 246.2 | 253.1 | 245.8 | 254.9 | 253.4 | 261.1 | 259.3 | 258.8 | 258.4 | 255.2 | 254.1833 | 261.1 | 245.8 | 247.4 | 253.7 | 254 | 246.3 | 249 | 260.6 | 252.7 | 249.9 | 257.4 | 252 | 258.8 | 259.9 | 253.475 | 260.6 | 246.3 | 246.4 | 257.9 | 259.2 | 258.8 | 256.6 | 257 | 256.2 | 255 | 256.3 | 249.1 | 259.4 | 231.8 | 253.6417 | 259.4 | 231.8
2026-05-03 | 09:45:00.000 | 267.6 | 264.2 | 266.4 | 261.1 | 261 | 260.3 | 255.6 | 269.8 | 264.5 | 265.5 | 262.8 | 260.8 | 263.3 | 269.8 | 255.6 | 244.1 | 242.6 | 235.6 | 221.4 | 218 | 258.2 | 250.1 | 245.7 | 241.3 | 231 | 220.6 | 224.9 | 236.125 | 258.2 | 218 | 264.2 | 270.7 | 275.3 | 276.6 | 265.1 | 260.5 | 258.8 | 264.1 | 270.6 | 275.6 | 276.2 | 251.4 | 267.425 | 276.6 | 251.4
2026-05-03 | 10:00:00.000 | 171 | 165.5 | 167.9 | 167.6 | 159.6 | 159.9 | 169.8 | 166.8 | 163.8 | 166.6 | 167.3 | 171 | 166.4 | 171 | 159.6 | 167.2 | 173.1 | 174.4 | 174.6 | 177.6 | 171.1 | 171.6 | 177.6 | 177.7 | 174.4 | 176.6 | 180.4 | 174.6917 | 180.4 | 167.2 | 171.2 | 160.7 | 161.5 | 183.2 | 165.9 | 172.8 | 161 | 158.8 | 171.9 | 174.6 | 173.9 | 152.5 | 167.3333 | 183.2 | 152.5
2026-05-03 | 10:15:00.000 | 178.9 | 188.4 | 196.5 | 198.8 | 199 | 188.3 | 189.9 | 194.5 | 197 | 197.3 | 186.1 | 183.7 | 191.5333 | 199 | 178.9 | 181.2 | 186 | 184 | 180.8 | 180.4 | 185.2 | 173.8 | 179.9 | 176.4 | 171.5 | 161.9 | 172.9 | 177.8333 | 186 | 161.9 | 179.8 | 175.6 | 183.9 | 184.9 | 182.1 | 171.1 | 163.9 | 171.3 | 177.6 | 177.1 | 186.6 | 161.5 | 176.2833 | 186.6 | 161.5
2026-05-03 | 10:30:00.000 | 169.1 | 163.3 | 170.5 | 172.6 | 161 | 167.6 | 176.3 | 159.3 | 170.8 | 171.8 | 172.9 | 175.2 | 169.2 | 176.3 | 159.3 | 175.1 | 180.2 | 180.9 | 173.8 | 165.6 | 178.4 | 178.5 | 178.9 | 172.1 | 179.6 | 184 | 186.1 | 177.7667 | 186.1 | 165.6 | 174.4 | 174.4 | 172.2 | 165.9 | 172.7 | 174.2 | 163 | 164.8 | 163.6 | 169.7 | 167.8 | 159 | 168.475 | 174.4 | 159
2026-05-03 | 10:45:00.000 | 208.2 | 211.2 | 208.5 | 206.3 | 207.8 | 207.7 | 200.8 | 215.5 | 204.6 | 205 | 207 | 203.9 | 207.2083 | 215.5 | 200.8 | 191.5 | 196.2 | 191.3 | 185.4 | 183.4 | 196.8 | 197.7 | 187.4 | 196.3 | 193.1 | 193.9 | 184.5 | 191.4583 | 197.7 | 183.4 | 208.3 | 210.9 | 209.9 | 212.7 | 213.5 | 212.8 | 218.9 | 209.2 | 216.3 | 214.3 | 215.3 | 212.8 | 212.9083 | 218.9 | 208.3
2026-05-03 | 11:00:00.000 | 158.3 | 160.4 | 162.1 | 159 | 162.1 | 162.5 | 159.9 | 164.5 | 164.8 | 166.4 | 167.6 | 165.2 | 162.7333 | 167.6 | 158.3 | 158.4 | 157.7 | 157.5 | 158.5 | 158.2 | 168.9 | 165.7 | 167.6 | 166.8 | 166 | 165.7 | 166.1 | 163.0917 | 168.9 | 157.5 | 164.3 | 159.7 | 156.2 | 153.5 | 148 | 148.1 | 151.6 | 151.8 | 158.8 | 161.9 | 160.9 | 146.8 | 155.1333 | 164.3 | 146.8
2026-05-03 | 11:15:00.000 | 105.7 | 105.9 | 105.3 | 104.5 | 106.2 | 105 | 105.5 | 105.8 | 102.3 | 105.8 | 102.4 | 106.2 | 105.05 | 106.2 | 102.3 | 106 | 102.5 | 106 | 106.2 | 106.2 | 105.7 | 105.9 | 106.3 | 106.1 | 106.2 | 105.5 | 105.5 | 105.675 | 106.3 | 102.5 | 106 | 106.2 | 106 | 106 | 105.8 | 103.7 | 104.8 | 104.1 | 105.6 | 104.9 | 105.6 | 102.8 | 105.125 | 106.2 | 102.8
2026-05-03 | 11:30:00.000 | 101.7 | 101.4 | 98.8 | 102.7 | 103.5 | 103.9 | 104.3 | 102.8 | 102.2 | 102.7 | 103 | 103.5 | 102.5417 | 104.3 | 98.8 | 104.4 | 104.8 | 104.8 | 105 | 104.5 | 103.5 | 103.1 | 103.9 | 104.1 | 100.6 | 103.9 | 104.3 | 103.9083 | 105 | 100.6 | 103.2 | 101.5 | 102.6 | 103.3 | 102.9 | 102.4 | 102.2 | 101.8 | 100.7 | 101.9 | 99.4 | 96.5 | 101.5333 | 103.3 | 96.5
2026-05-03 | 11:45:00.000 | 106 | 106 | 105.8 | 105.8 | 106 | 106.1 | 105.8 | 106.2 | 106.1 | 106.4 | 106.1 | 105.9 | 106.0167 | 106.4 | 105.8 | 105.8 | 105.7 | 105.6 | 106 | 105.4 | 106 | 105.6 | 105.5 | 105.9 | 106 | 106 | 105.3 | 105.7333 | 106 | 105.3 | 105.6 | 106.1 | 105.6 | 106.1 | 102.4 | 106.1 | 106.2 | 105.9 | 105.9 | 106.1 | 105.9 | 105.9 | 105.65 | 106.2 | 102.4
2026-05-03 | 12:00:00.000 | 106 | 106.1 | 105.8 | 105.8 | 106.1 | 106.2 | 105.8 | 106.3 | 106.1 | 106.1 | 106.1 | 106 | 106.0333 | 106.3 | 105.8 | 105.8 | 105.7 | 105.6 | 106 | 105.5 | 106 | 105.6 | 105.5 | 105.9 | 106 | 106 | 105.4 | 105.75 | 106 | 105.4 | 105.6 | 106.1 | 105.5 | 105.7 | 106.1 | 106 | 106.2 | 106.1 | 105.9 | 106 | 105.9 | 105.8 | 105.9083 | 106.2 | 105.5
2026-05-03 | 12:15:00.000 | 105.4 | 105.4 | 105.6 | 105.6 | 102 | 105.9 | 105.9 | 106.4 | 106.1 | 106 | 106.1 | 105.7 | 105.5083 | 106.4 | 102 | 105 | 105.7 | 105.3 | 104.8 | 104.7 | 106.2 | 105.8 | 102.1 | 106 | 105.8 | 106.1 | 105.5 | 105.25 | 106.2 | 102.1 | 105.7 | 106.1 | 105.6 | 105.7 | 106.2 | 106.2 | 106.2 | 105.9 | 106 | 102.5 | 105.9 | 104.7 | 105.5583 | 106.2 | 102.5
2026-05-03 | 12:30:00.000 | 105.7 | 105.9 | 106 | 105.9 | 106.3 | 106.4 | 106.3 | 106.3 | 106.1 | 106.2 | 106.2 | 105.9 | 106.1 | 106.4 | 105.7 | 106 | 106.1 | 105.5 | 105.6 | 105.6 | 106.1 | 106 | 105.5 | 106 | 106.2 | 106.1 | 105.4 | 105.8417 | 106.2 | 105.4 | 105.6 | 106.1 | 105.5 | 105.7 | 106.1 | 106.1 | 106.2 | 106.1 | 105.9 | 106 | 105.9 | 105.9 | 105.925 | 106.2 | 105.5
2026-05-03 | 12:45:00.000 | 103.8 | 104.5 | 104.8 | 105.5 | 106.3 | 106.4 | 106.3 | 104.8 | 105.3 | 106.1 | 106.4 | 105.9 | 105.5083 | 106.4 | 103.8 | 106 | 106.1 | 105.5 | 105.6 | 105.6 | 106.1 | 106 | 105.5 | 106 | 106.2 | 106.1 | 105.4 | 105.8417 | 106.2 | 105.4 | 105.1 | 106.1 | 101.9 | 105.7 | 105.9 | 106.1 | 105.4 | 105.9 | 104.9 | 103.7 | 103.4 | 103.8 | 104.825 | 106.1 | 101.9
2026-05-03 | 13:00:00.000 | 106.1 | 106.1 | 105.2 | 105.9 | 106.1 | 106.4 | 106.2 | 106.2 | 106 | 106 | 106.2 | 105.9 | 106.025 | 106.4 | 105.2 | 106 | 106.1 | 105.5 | 105.6 | 105.5 | 106 | 106 | 105.5 | 105.9 | 106.1 | 106 | 105.4 | 105.8 | 106.1 | 105.4 | 105 | 106.1 | 105.6 | 106 | 105.8 | 106 | 106.5 | 106.1 | 106.1 | 106.2 | 105.9 | 106 | 105.9417 | 106.5 | 105
2026-05-03 | 13:15:00.000 | 106 | 105.9 | 106.2 | 105.9 | 106 | 106.3 | 106.2 | 106.2 | 106 | 106 | 106.2 | 105.9 | 106.0667 | 106.3 | 105.9 | 106 | 106 | 105.5 | 105.6 | 105.6 | 106 | 106 | 105.5 | 105.9 | 106.2 | 106.1 | 105.4 | 105.8167 | 106.2 | 105.4 | 105.7 | 106.1 | 105.6 | 106 | 105.8 | 106 | 106.1 | 106 | 106 | 106.2 | 105.9 | 106 | 105.95 | 106.2 | 105.6
2026-05-03 | 13:30:00.000 | 105.9 | 105.8 | 106.2 | 105.8 | 102.3 | 106.3 | 106.2 | 106.1 | 105.9 | 105.9 | 106.2 | 105.8 | 105.7 | 106.3 | 102.3 | 105.9 | 106 | 105.4 | 105.5 | 105.5 | 106 | 105.9 | 105.4 | 105.9 | 106.1 | 106 | 105.4 | 105.75 | 106.1 | 105.4 | 105.7 | 106 | 105.5 | 105.9 | 105.7 | 105.9 | 106.1 | 106 | 106 | 102.6 | 105.9 | 105.9 | 105.6 | 106.1 | 102.6
2026-05-03 | 13:45:00.000 | 230.9 | 228.1 | 227.4 | 229.9 | 230.1 | 228 | 230.7 | 241.5 | 238.6 | 236.7 | 236.2 | 230.8 | 232.4083 | 241.5 | 227.4 | 218.7 | 227.9 | 227 | 218.8 | 222.8 | 238.3 | 223.5 | 234.8 | 224 | 223.4 | 223.4 | 233.9 | 226.375 | 238.3 | 218.7 | 242.2 | 242.6 | 239.1 | 240.1 | 239 | 237.1 | 243.7 | 237.6 | 235.3 | 235.9 | 243.6 | 223.6 | 238.3167 | 243.7 | 223.6
2026-05-03 | 14:00:00.000 | 245.8 | 244.5 | 244 | 247.2 | 244.7 | 246.5 | 249.8 | 253.5 | 251.4 | 249.6 | 250.4 | 245.3 | 247.725 | 253.5 | 244 | 241.4 | 247.6 | 248.8 | 242.1 | 245.1 | 251.6 | 241.3 | 250.4 | 248.7 | 241.1 | 250.1 | 249.9 | 246.5083 | 251.6 | 241.1 | 247.2 | 255 | 255.4 | 246.8 | 255.8 | 255.5 | 256.2 | 252.1 | 252.6 | 252.9 | 252.6 | 241 | 251.925 | 256.2 | 241
2026-05-03 | 14:15:00.000 | 281.2 | 271.9 | 281.3 | 280.9 | 270.7 | 281.3 | 281.7 | 281.3 | 281.2 | 281.6 | 281.4 | 281.1 | 279.6333 | 281.7 | 270.7 | 281.1 | 281.6 | 281.6 | 281.2 | 281.6 | 281.8 | 281.6 | 281.3 | 281.5 | 271.6 | 281.2 | 281.2 | 280.6083 | 281.8 | 271.6 | 281.4 | 281.5 | 281.8 | 281.7 | 281.6 | 280.6 | 281.7 | 281.3 | 281.4 | 281.3 | 281.3 | 281.4 | 281.4167 | 281.8 | 280.6
2026-05-03 | 14:30:00.000 | 281 | 280.8 | 281.2 | 280.8 | 280.6 | 281.2 | 281.4 | 280.2 | 281 | 281.1 | 281.3 | 281 | 280.9667 | 281.4 | 280.2 | 279 | 281.3 | 280.9 | 279.7 | 279.9 | 281.6 | 280.9 | 281.2 | 281.4 | 280.8 | 281.1 | 280.9 | 280.725 | 281.6 | 279 | 281.2 | 281.5 | 271.9 | 281.6 | 281.6 | 281 | 281.5 | 281.2 | 281.4 | 281.3 | 270.7 | 280.3 | 279.6 | 281.6 | 270.7
2026-05-03 | 14:45:00.000 | 277.5 | 276.7 | 266.5 | 277.9 | 275.6 | 275.7 | 277.6 | 279.9 | 279.7 | 277.7 | 277.3 | 277.4 | 276.625 | 279.9 | 266.5 | 271.5 | 273.3 | 274.7 | 270.5 | 272.3 | 278 | 275.2 | 268.5 | 278.8 | 275 | 272.9 | 278.3 | 274.0833 | 278.8 | 268.5 | 279 | 269.9 | 279.6 | 279.9 | 280.1 | 279.3 | 280.3 | 278.5 | 278.3 | 278.8 | 279.4 | 272.6 | 277.975 | 280.3 | 269.9
2026-05-03 | 15:00:00.000 | 277.7 | 276.5 | 277.1 | 277.5 | 276.9 | 276.5 | 276.6 | 280.4 | 270.5 | 278.9 | 278.9 | 278.1 | 277.1333 | 280.4 | 270.5 | 272.5 | 269.5 | 274.8 | 272.1 | 263.4 | 279.2 | 275.8 | 278.3 | 278.5 | 274 | 265.2 | 279.1 | 273.5333 | 279.2 | 263.4 | 280.3 | 271.2 | 280.6 | 280.6 | 281 | 280.2 | 280.8 | 280.8 | 279.8 | 280.1 | 281.1 | 273.5 | 279.1667 | 281.1 | 271.2
2026-05-03 | 15:15:00.000 | 279.7 | 279.3 | 278.8 | 278.5 | 280.4 | 279.3 | 277.8 | 280.6 | 279.5 | 280.6 | 280.7 | 279.2 | 279.5333 | 280.7 | 277.8 | 277.3 | 277.8 | 279.1 | 273.9 | 275 | 280.4 | 266.8 | 280.3 | 280.6 | 278.5 | 278.6 | 278.9 | 277.2667 | 280.6 | 266.8 | 281.6 | 280.6 | 280.8 | 280.7 | 280.6 | 280.4 | 281.1 | 280.6 | 281 | 280.7 | 280.7 | 279.4 | 280.6833 | 281.6 | 279.4
2026-05-03 | 15:30:00.000 | 281 | 280.8 | 280.5 | 280.5 | 280.8 | 280.4 | 281.2 | 281.4 | 281.4 | 280.9 | 281.7 | 280.6 | 280.9333 | 281.7 | 280.4 | 280.9 | 281.2 | 281.3 | 279.9 | 280.7 | 281.3 | 280.3 | 281 | 281.1 | 280.7 | 281 | 281.2 | 280.8833 | 281.3 | 279.9 | 281.4 | 281.9 | 281.3 | 281.3 | 281.4 | 281.2 | 281.9 | 280.8 | 281.1 | 281.2 | 272 | 280.7 | 280.5167 | 281.9 | 272
2026-05-03 | 15:45:00.000 | 280.7 | 281.1 | 280.8 | 280.8 | 281.2 | 280.4 | 280.5 | 281.4 | 281.3 | 281.3 | 280.8 | 280.7 | 280.9167 | 281.4 | 280.4 | 278.8 | 280.4 | 280.8 | 278.5 | 279.5 | 281.7 | 280.4 | 281 | 280.8 | 280 | 281.5 | 281.3 | 280.3917 | 281.7 | 278.5 | 281.5 | 281.3 | 281 | 281.1 | 281.6 | 281.9 | 281.4 | 281 | 281 | 271.6 | 281.1 | 279.7 | 280.35 | 281.9 | 271.6
2026-05-03 | 16:00:00.000 | 270.3 | 270.1 | 270.1 | 271.3 | 272.4 | 270.3 | 263.7 | 266 | 273.5 | 274.6 | 272.8 | 271.5 | 270.55 | 274.6 | 263.7 | 267.6 | 270.4 | 270.6 | 258.1 | 268.4 | 275.3 | 269.1 | 273 | 273.5 | 270.1 | 274.3 | 274.4 | 270.4 | 275.3 | 258.1 | 275.7 | 273.3 | 273.9 | 274 | 272.5 | 272.8 | 273.4 | 270.9 | 272.6 | 273.3 | 273.6 | 266.7 | 272.725 | 275.7 | 266.7
2026-05-03 | 16:15:00.000 | 264.7 | 263.2 | 252.8 | 264.8 | 261.3 | 260 | 265.1 | 273.2 | 271.9 | 257.1 | 257.7 | 256.9 | 262.3917 | 273.2 | 252.8 | 243.4 | 261.4 | 258.4 | 253.9 | 256.3 | 269.6 | 260.6 | 266.4 | 266.8 | 259.8 | 270.1 | 262.4 | 260.7583 | 270.1 | 243.4 | 266.5 | 273.3 | 242.9 | 272.6 | 262.8 | 272.2 | 275.7 | 272.1 | 272.7 | 271.4 | 273.8 | 258.8 | 267.9 | 275.7 | 242.9
2026-05-03 | 16:30:00.000 | 248 | 246.1 | 247.6 | 247.3 | 242 | 249.3 | 249.3 | 254.1 | 252.5 | 255 | 253 | 249.7 | 249.4917 | 255 | 242 | 241.4 | 248.3 | 248 | 242.8 | 245.8 | 253 | 246.4 | 250.4 | 252.7 | 247 | 255.3 | 255.9 | 248.9167 | 255.9 | 241.4 | 257.2 | 251.7 | 252.1 | 251.6 | 251.4 | 240.2 | 254 | 250.1 | 243.7 | 252.5 | 253.7 | 240.6 | 249.9 | 257.2 | 240.2
2026-05-03 | 16:45:00.000 | 155 | 152.8 | 153.3 | 154.6 | 156.4 | 155.4 | 151.1 | 161.5 | 160.5 | 160.5 | 158.6 | 158.5 | 156.5167 | 161.5 | 151.1 | 149.7 | 156.9 | 154.5 | 151.1 | 150.4 | 161.1 | 153.7 | 159.4 | 160.1 | 154.8 | 165.1 | 166.2 | 156.9167 | 166.2 | 149.7 | 163.8 | 159.5 | 153.3 | 160.2 | 157.2 | 158.2 | 159.8 | 156.7 | 157.9 | 158.5 | 161.9 | 146.5 | 157.7917 | 163.8 | 146.5
2026-05-03 | 17:00:00.000 | 170.9 | 168.2 | 161.8 | 167.8 | 168.7 | 167.4 | 167.9 | 175.9 | 174.6 | 173.4 | 172.5 | 171.5 | 170.05 | 175.9 | 161.8 | 160.6 | 166.3 | 165 | 162.1 | 165.8 | 173.4 | 163.5 | 172.3 | 173.8 | 168.7 | 175.1 | 176.7 | 168.6083 | 176.7 | 160.6 | 179.4 | 177.1 | 176.1 | 178 | 177 | 178.5 | 179.4 | 174.7 | 175.8 | 175.6 | 178.7 | 167 | 176.4417 | 179.4 | 167
2026-05-03 | 17:15:00.000 | 153.7 | 151.5 | 150.2 | 149.9 | 148.6 | 146.3 | 147.4 | 159.9 | 158.4 | 153.7 | 152.3 | 150.8 | 151.8917 | 159.9 | 146.3 | 138.1 | 144.5 | 141.5 | 138.6 | 141.7 | 151.9 | 144.6 | 150.3 | 151.7 | 140.8 | 151.3 | 152.1 | 145.5917 | 152.1 | 138.1 | 162.6 | 160.1 | 159.2 | 161.3 | 161.5 | 157.1 | 167.1 | 162.3 | 160.9 | 159.6 | 164.3 | 146.9 | 160.2417 | 167.1 | 146.9
2026-05-03 | 17:30:00.000 | 102.9 | 102.3 | 100.9 | 101.5 | 101.4 | 99.8 | 100.6 | 107.6 | 107 | 105.4 | 104.5 | 103.6 | 103.125 | 107.6 | 99.8 | 96.2 | 100 | 98.5 | 95.9 | 98.1 | 105.5 | 100.4 | 100.6 | 104 | 100.7 | 105.6 | 106.4 | 100.9917 | 106.4 | 95.9 | 109.7 | 108.9 | 107 | 108.5 | 107.9 | 109.2 | 111.3 | 107.4 | 107.2 | 107 | 110.4 | 99.9 | 107.8667 | 111.3 | 99.9
2026-05-03 | 17:45:00.000 | 86.9 | 85.9 | 86 | 86.1 | 86.2 | 84.9 | 85.3 | 91.7 | 87.5 | 89.3 | 88.7 | 87.4 | 87.1583 | 91.7 | 84.9 | 81.6 | 84.9 | 83.8 | 81.3 | 82.7 | 89.3 | 85.3 | 88.4 | 88.7 | 85.3 | 89.3 | 89.8 | 85.8667 | 89.8 | 81.3 | 92.8 | 90.8 | 90.9 | 91.2 | 90.6 | 91.7 | 92.8 | 90.4 | 91.1 | 90.8 | 92.2 | 85.2 | 90.875 | 92.8 | 85.2
2026-05-03 | 18:00:00.000 | 78.4 | 77.3 | 77.3 | 77.1 | 76.8 | 75.8 | 75.7 | 82.8 | 81.5 | 80.4 | 79.8 | 78.2 | 78.425 | 82.8 | 75.7 | 72.4 | 75.5 | 74.2 | 72 | 73.1 | 80.1 | 76.4 | 78.8 | 79.1 | 75.9 | 79.2 | 79.7 | 76.3667 | 80.1 | 72 | 84.5 | 83.6 | 83.7 | 84.8 | 84.5 | 85.7 | 86 | 83.1 | 83.6 | 83.7 | 84.1 | 78.2 | 83.7917 | 86 | 78.2
2026-05-03 | 18:15:00.000 | 87.8 | 87.1 | 87.1 | 87.7 | 87.8 | 86.7 | 85.6 | 95.4 | 94.3 | 92.9 | 92.6 | 89.7 | 89.5583 | 95.4 | 85.6 | 83.4 | 87.3 | 86.1 | 82.6 | 83.7 | 90.6 | 86.6 | 89.4 | 89.7 | 85.8 | 89.1 | 89.8 | 87.0083 | 90.6 | 82.6 | 96.9 | 96.9 | 95.3 | 94.9 | 94.1 | 94.4 | 96.3 | 93.8 | 95.3 | 96.1 | 96 | 86.1 | 94.675 | 96.9 | 86.1
2026-05-03 | 18:30:00.000 | 112.3 | 111.8 | 111.7 | 113 | 112.8 | 110.9 | 108.7 | 123.9 | 122 | 119.7 | 116.1 | 113.4 | 114.6917 | 123.9 | 108.7 | 106.5 | 111.6 | 110.5 | 104.9 | 105.6 | 113 | 108.4 | 111.1 | 111 | 105.7 | 108.5 | 109.8 | 108.8833 | 113 | 104.9 | 126.4 | 126.7 | 122.3 | 120 | 118.8 | 120.3 | 123.9 | 120.9 | 124.7 | 127.6 | 124.6 | 107.7 | 121.9917 | 127.6 | 107.7
2026-05-03 | 18:45:00.000 | 49.7 | 49.1 | 49.1 | 49.5 | 49.1 | 48.5 | 48.9 | 53.8 | 52.9 | 51.9 | 51.6 | 50.1 | 50.35 | 53.8 | 48.5 | 46.1 | 48.3 | 47.5 | 45.3 | 45.7 | 50 | 47.7 | 49.2 | 48.9 | 46.4 | 47.8 | 48.2 | 47.5917 | 50 | 45.3 | 54.9 | 55.1 | 54.2 | 54.3 | 54 | 54.1 | 55.3 | 53.6 | 54.9 | 55.8 | 54.7 | 50.2 | 54.2583 | 55.8 | 50.2
2026-05-03 | 19:00:00.000 | 34.6 | 34.3 | 34.4 | 34.9 | 34.7 | 34.6 | 35.2 | 37.4 | 37 | 36.5 | 36.3 | 35.7 | 35.4667 | 37.4 | 34.3 | 32.9 | 34.7 | 34.1 | 32.6 | 32.9 | 35.8 | 34.1 | 35.3 | 35.2 | 33.4 | 34.8 | 35.1 | 34.2417 | 35.8 | 32.6 | 38.1 | 38 | 37.7 | 37.6 | 37.3 | 36.9 | 37.6 | 36.7 | 37.5 | 37.9 | 37.9 | 34 | 37.2667 | 38.1 | 34
2026-05-03 | 19:15:00.000 | 52.5 | 52 | 51.8 | 53.3 | 53.1 | 51.5 | 53.3 | 61.9 | 60.7 | 59 | 58.9 | 54.5 | 55.2083 | 61.9 | 51.5 | 49.2 | 52.7 | 51.1 | 46.7 | 47.6 | 51 | 48.9 | 50.7 | 49.9 | 47 | 46.8 | 48.8 | 49.2 | 52.7 | 46.7 | 62.4 | 64.6 | 60.9 | 60.1 | 59.1 | 58.3 | 61.4 | 59.8 | 63.3 | 66 | 59.7 | 55.5 | 60.925 | 66 | 55.5
2026-05-03 | 19:30:00.000 | 27.3 | 27 | 27 | 27.8 | 27.2 | 26.4 | 27.7 | 31.9 | 31.1 | 30.3 | 30 | 28.2 | 28.4917 | 31.9 | 26.4 | 25.2 | 26.9 | 26.1 | 23.9 | 24.5 | 26.9 | 26 | 27.1 | 26.8 | 25.4 | 25.8 | 26.6 | 25.9333 | 27.1 | 23.9 | 32.7 | 33.7 | 31.8 | 31.6 | 31.2 | 29.8 | 31.7 | 30.7 | 32.9 | 34.9 | 31.2 | 29.3 | 31.7917 | 34.9 | 29.3
2026-05-03 | 19:45:00.000 | 7.6 | 7.5 | 7.6 | 7.7 | 7.7 | 7.7 | 7.6 | 8.1 | 8 | 7.9 | 7.8 | 7.7 | 7.7417 | 8.1 | 7.5 | 7.4 | 7.8 | 7.6 | 7.3 | 7.4 | 8.1 | 7.9 | 8.2 | 8.2 | 7.9 | 8.3 | 8.4 | 7.875 | 8.4 | 7.3 | 8.1 | 8 | 8.1 | 8 | 8 | 7.8 | 8 | 7.9 | 8.1 | 8.3 | 8.1 | 7.4 | 7.9833 | 8.3 | 7.4
2026-05-03 | 20:00:00.000 | 1.8 | 1.6 | 1.8 | 1.9 | 1.7 | 1.9 | 1.9 | 1.9 | 2 | 2 | 1.9 | 1.8 | 1.85 | 2 | 1.6 | 1.7 | 1.8 | 1.7 | 1.7 | 1.7 | 1.9 | 1.9 | 1.8 | 2 | 1.9 | 1.9 | 1.9 | 1.825 | 2 | 1.7 | 1.9 | 1.8 | 1.9 | 1.9 | 2 | 1.9 | 1.9 | 1.9 | 2 | 2 | 1.9 | 1.8 | 1.9083 | 2 | 1.8
2026-05-03 | 20:15:00.000 | 0.1 | 0.1 | 0.3 | 0.3 | 0.2 | 0.2 | 0.4 | 0.3 | 0.4 | 0.3 | 0.2 | 0.5 | 0.275 | 0.5 | 0.1 | 0.2 | 0.4 | 0.6 | 0.3 | 0.7 | 0.3 | 0.4 | 0.3 | 0.5 | 0.3 | 0.2 | 0.5 | 0.39167 | 0.7 | 0.2 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.3 | 0.45 | 0.8 | 0.3
2026-05-03 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.16667 | 0.8 | 0.1 | 0.1 | 0.1 | 0.6 | 0.1 | 0.5 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.7 | 0.275 | 0.7 | 0.1 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13333 | 0.5 | 0.1
2026-05-03 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.2 | 0 | 0 | 0 | 0.3 | 0 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0
2026-05-03 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-03 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320