## PR_Calc
PR CALCULATION
04 MAGGIO 2026 | [67 empty] | 4 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 48
RAW PR | [64 empty] | 0.84648 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 84.6476
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 84.7124
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 84.6396
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-04 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10781.5
2026-05-04 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 00:30:00.000 | -0.8 | -0.0002 | 0 | 0 | -0.0001 | 0 | -0.0001 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 00:45:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 01:45:00.000 | -0.9 | -0.000225 | 0 | 0 | -0.0001125 | 0 | -0.0001125 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 02:00:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 02:15:00.000 | -0.8 | -0.0002 | -0.2 | -5e-05 | -0.000125 | 0 | -0.000125 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 02:30:00.000 | -1 | -0.00025 | -0.7 | -0.000175 | -0.0002125 | 0 | -0.0002125 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 02:45:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 03:15:00.000 | -0.7 | -0.000175 | 0 | 0 | -8.75e-05 | 0 | -8.75e-05 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 03:30:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 03:45:00.000 | -0.6 | -0.00015 | -0.3 | -7.5e-05 | -0.0001125 | 0 | -0.0001125 | 0 | 30290.4 | 30290.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 04:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 04:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 04:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 04:45:00.000 | -1 | -0.00025 | -0.2 | -5e-05 | -0.00015 | 0 | -0.00015 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 05:00:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 05:15:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 05:30:00.000 | -1 | -0.00025 | -0.3 | -7.5e-05 | -0.0001625 | 0 | -0.0001625 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 05:45:00.000 | -1 | -0.00025 | -0.9 | -0.000225 | -0.0002375 | 0 | -0.0002375 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 06:00:00.000 | -0.7 | -0.000175 | -0.5 | -0.000125 | -0.00015 | 0 | -0.00015 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 06:15:00.000 | 1.8 | 0.00045 | 2 | 0.0005 | 0.000475 | 0 | 0.000475 | 0.10526 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 06:30:00.000 | 8.8 | 0.0022 | 8.8 | 0.0022 | 0.0022 | 0 | 0.0022 | 0 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 06:45:00.000 | 20.8 | 0.0052 | 20.3 | 0.005075 | 0.0051375 | 0 | 0.0051375 | 0.024331 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 07:00:00.000 | 31.9 | 0.007975 | 32.5 | 0.008125 | 0.00805 | 0 | 0.00805 | 0.018634 | 30290.4 | 30290.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 07:15:00.000 | 133.3 | 0.033325 | 132.3 | 0.033075 | 0.0332 | 132.8 | 0.033325 | 0.0075301 | 30290.4 | 30290.6 | 200 | 0.876 | 0 | 9.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76439 | 9.1727 | 0 | 9.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 07:30:00.000 | 235.9 | 0.058975 | 232.5 | 0.058125 | 0.05855 | 234.2 | 0.058975 | 0.014518 | 30290.6 | 30291.1 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 07:45:00.000 | 110.9 | 0.027725 | 109.5 | 0.027375 | 0.02755 | 110.2 | 0.027725 | 0.012704 | 30291.1 | 30291.6 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 08:00:00.000 | 273.7 | 0.068425 | 296.7 | 0.074175 | 0.0713 | 285.2 | 0.074175 | 0.080645 | 30291.6 | 30292.1 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 08:15:00.000 | 501.5 | 0.12537 | 511.9 | 0.12798 | 0.12667 | 506.7 | 0.12798 | 0.020525 | 30292.1 | 30293.2 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 08:30:00.000 | 616.2 | 0.15405 | 620.3 | 0.15507 | 0.15456 | 618.25 | 0.15507 | 0.0066316 | 30293.2 | 30294.9 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 08:45:00.000 | 751 | 0.18775 | 762.2 | 0.19055 | 0.18915 | 756.6 | 0.19055 | 0.014803 | 30294.9 | 30296.9 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 09:00:00.000 | 862.5 | 0.21563 | 862.6 | 0.21565 | 0.21564 | 862.55 | 0.21565 | 0.00011594 | 30296.9 | 30299.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 09:15:00.000 | 864.6 | 0.21615 | 856.1 | 0.21402 | 0.21509 | 860.35 | 0.21615 | 0.0098797 | 30299.2 | 30301.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 09:30:00.000 | 928.8 | 0.2322 | 919.1 | 0.22978 | 0.23099 | 923.95 | 0.2322 | 0.010498 | 30301.6 | 30304 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 09:45:00.000 | 946.2 | 0.23655 | 934.4 | 0.2336 | 0.23508 | 940.3 | 0.23655 | 0.012549 | 30304 | 30306.5 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 10:00:00.000 | 960.6 | 0.24015 | 946.2 | 0.23655 | 0.23835 | 953.4 | 0.24015 | 0.015104 | 30306.5 | 30309 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 10:15:00.000 | 969.1 | 0.24228 | 952.7 | 0.23817 | 0.24023 | 960.9 | 0.24228 | 0.017067 | 30309 | 30311.5 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 10:30:00.000 | 974.9 | 0.24372 | 957.2 | 0.2393 | 0.24151 | 966.05 | 0.24372 | 0.018322 | 30311.5 | 30314 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 10:45:00.000 | 966.1 | 0.24153 | 949.2 | 0.2373 | 0.23941 | 957.65 | 0.24153 | 0.017647 | 30314 | 30316.4 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 11:00:00.000 | 979 | 0.24475 | 957.5 | 0.23938 | 0.24206 | 968.25 | 0.24475 | 0.022205 | 30316.4 | 30318.9 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 11:15:00.000 | 980.5 | 0.24513 | 956.9 | 0.23922 | 0.24218 | 968.7 | 0.24513 | 0.024363 | 30318.9 | 30321.4 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 11:30:00.000 | 979.1 | 0.24477 | 953.5 | 0.23838 | 0.24157 | 966.3 | 0.24477 | 0.026493 | 30321.4 | 30323.9 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 11:45:00.000 | 974.6 | 0.24365 | 948.7 | 0.23718 | 0.24041 | 961.65 | 0.24365 | 0.026933 | 30323.9 | 30326.4 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 12:00:00.000 | 973.9 | 0.24347 | 946.6 | 0.23665 | 0.24006 | 960.25 | 0.24347 | 0.02843 | 30326.4 | 30328.9 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 12:15:00.000 | 969.9 | 0.24247 | 942.3 | 0.23557 | 0.23902 | 956.1 | 0.24247 | 0.028867 | 30328.9 | 30331.4 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 12:30:00.000 | 967.6 | 0.2419 | 939.6 | 0.2349 | 0.2384 | 953.6 | 0.2419 | 0.029362 | 30331.4 | 30333.8 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 12:45:00.000 | 959.3 | 0.23982 | 911.4 | 0.22785 | 0.23384 | 935.35 | 0.23982 | 0.051211 | 30333.8 | 30336.3 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 13:00:00.000 | 965.7 | 0.24143 | 936.3 | 0.23407 | 0.23775 | 951 | 0.24143 | 0.030915 | 30336.3 | 30338.8 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 13:15:00.000 | 965 | 0.24125 | 935.7 | 0.23393 | 0.23759 | 950.35 | 0.24125 | 0.030831 | 30338.8 | 30341.3 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 13:30:00.000 | 966 | 0.2415 | 937.1 | 0.23428 | 0.23789 | 951.55 | 0.2415 | 0.030371 | 30341.3 | 30343.8 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 13:45:00.000 | 963.9 | 0.24097 | 935.8 | 0.23395 | 0.23746 | 949.85 | 0.24097 | 0.029584 | 30343.8 | 30346.3 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 14:00:00.000 | 962 | 0.2405 | 935.3 | 0.23382 | 0.23716 | 948.65 | 0.2405 | 0.028145 | 30346.3 | 30348.7 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 14:15:00.000 | 975.8 | 0.24395 | 950.2 | 0.23755 | 0.24075 | 963 | 0.24395 | 0.026584 | 30348.7 | 30351.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 14:30:00.000 | 981.5 | 0.24538 | 956.9 | 0.23922 | 0.2423 | 969.2 | 0.24538 | 0.025382 | 30351.2 | 30353.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 14:45:00.000 | 982.5 | 0.24563 | 957.4 | 0.23935 | 0.24249 | 969.95 | 0.24563 | 0.025878 | 30353.7 | 30356.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 15:00:00.000 | 975.2 | 0.2438 | 950.5 | 0.23763 | 0.24071 | 962.85 | 0.2438 | 0.025653 | 30356.2 | 30358.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 15:15:00.000 | 978.7 | 0.24468 | 955.5 | 0.23888 | 0.24178 | 967.1 | 0.24468 | 0.023989 | 30358.7 | 30361.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 15:30:00.000 | 1014.9 | 0.25372 | 988 | 0.247 | 0.25036 | 1001.45 | 0.25372 | 0.026861 | 30361.2 | 30363.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 15:45:00.000 | 961.3 | 0.24032 | 925.3 | 0.23132 | 0.23582 | 943.3 | 0.24032 | 0.038164 | 30363.7 | 30366.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 16:00:00.000 | 962.1 | 0.24053 | 933.1 | 0.23328 | 0.2369 | 947.6 | 0.24053 | 0.030604 | 30366.1 | 30368.5 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 16:15:00.000 | 973.5 | 0.24338 | 945.4 | 0.23635 | 0.23986 | 959.45 | 0.24338 | 0.029288 | 30368.5 | 30370.9 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 16:30:00.000 | 970.8 | 0.2427 | 947 | 0.23675 | 0.23972 | 958.9 | 0.2427 | 0.02482 | 30370.9 | 30373.4 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 16:45:00.000 | 954.4 | 0.2386 | 929.1 | 0.23228 | 0.23544 | 941.75 | 0.2386 | 0.026865 | 30373.4 | 30375.9 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 17:00:00.000 | 952.4 | 0.2381 | 926.9 | 0.23172 | 0.23491 | 939.65 | 0.2381 | 0.027138 | 30375.9 | 30378.3 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 17:15:00.000 | 808 | 0.202 | 812.9 | 0.20322 | 0.20261 | 810.45 | 0.20322 | 0.006046 | 30378.3 | 30380.6 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 17:30:00.000 | 550.3 | 0.13757 | 583.1 | 0.14578 | 0.14167 | 566.7 | 0.14578 | 0.057879 | 30380.6 | 30382.5 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 17:45:00.000 | 406.5 | 0.10162 | 431.9 | 0.10797 | 0.1048 | 419.2 | 0.10797 | 0.060592 | 30382.5 | 30383.8 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 18:00:00.000 | 211.8 | 0.05295 | 221.3 | 0.055325 | 0.054138 | 216.55 | 0.055325 | 0.04387 | 30383.8 | 30384.8 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 18:15:00.000 | 118.2 | 0.02955 | 115.5 | 0.028875 | 0.029213 | 116.85 | 0.02955 | 0.023107 | 30384.8 | 30385.2 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 18:30:00.000 | 85.5 | 0.021375 | 82.9 | 0.020725 | 0.02105 | 84.2 | 0.021375 | 0.030879 | 30385.2 | 30385.5 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 18:45:00.000 | 66.6 | 0.01665 | 65.2 | 0.0163 | 0.016475 | 65.9 | 0.01665 | 0.021244 | 30385.5 | 30385.7 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 19:00:00.000 | 55.8 | 0.01395 | 54.3 | 0.013575 | 0.013762 | 55.05 | 0.01395 | 0.027248 | 30385.7 | 30385.9 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 19:15:00.000 | 21.6 | 0.0054 | 21.6 | 0.0054 | 0.0054 | 0 | 0.0054 | 0 | 30385.9 | 30386 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 19:30:00.000 | 17.8 | 0.00445 | 20 | 0.005 | 0.004725 | 0 | 0.004725 | 0.1164 | 30386 | 30386 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 19:45:00.000 | 27.3 | 0.006825 | 28.8 | 0.0072 | 0.0070125 | 0 | 0.0070125 | 0.053476 | 30386 | 30386.1 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 20:00:00.000 | 8.2 | 0.00205 | 8.4 | 0.0021 | 0.002075 | 0 | 0.002075 | 0.024096 | 30386.1 | 30386.2 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 20:15:00.000 | 0.3 | 7.5e-05 | 0.3 | 7.5e-05 | 7.5e-05 | 0 | 7.5e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 20:30:00.000 | -0.8 | -0.0002 | -0.7 | -0.000175 | -0.0001875 | 0 | -0.0001875 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 20:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 21:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 21:15:00.000 | -0.2 | -5e-05 | -0.1 | -2.5e-05 | -3.75e-05 | 0 | -3.75e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 21:30:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 21:45:00.000 | -1 | -0.00025 | -0.7 | -0.000175 | -0.0002125 | 0 | -0.0002125 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 22:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 22:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 22:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 22:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 23:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 23:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 23:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
2026-05-04 | 23:45:00.000 | -1 | -0.00025 | -0.2 | -5e-05 | -0.00015 | 0 | -0.00015 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98538
PR for each inverter |  |  | 9.1997 |  | 9.0345 | 9.1171 |  | 9.2319 |  |  |  | 95800 |  | 0.86285 | 0.85636 | 0.86215 | 0.86208 | 0.86278 | 0.86124 | 0.86273 | 0.8337 | 0.83333 | 0.82775 | 0.82816 | 0.86492 | #DIV/0! | #DIV/0! | #DIV/0! | 9.1727 | 0.89368 | 0.85802 | 0.85765 | 0.89212 | 0.89555 | 0.82903 | 0.82896 | 0.82141 | 0.82718 | 0.86042 | 0.82527 | 0.82265 |  |  |  | 0 | 0.83208 | 0.83182 | 0.83343 | 0.83294 | 0.83251 | 0.82855 | 0.83616 | 0.83388 | 0.83372 | 0.83462 | 0.83504 | 0.90173 | #DIV/0! | #DIV/0! | #DIV/0! | 0 |  | 0.84712 |  | #DIV/0! | #DIV/0! | 7.0779e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-04 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 06:30:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 1.3 | 0 | 0.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.9 | 1.3 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 0
2026-05-04 | 06:45:00.000 | 1.4 | 1.2 | 1.7 | 1.5 | 4.9 | 1.4 | 1.7 | 1.5 | 4.5 | 1.5 | 1.6 | 4.5 | 2.2833 | 4.9 | 1.2 | 3.8 | 1.3 | 4.6 | 4.6 | 4.6 | 4.2 | 4.6 | 5.2 | 4.8 | 4.4 | 4.5 | 4.9 | 4.2917 | 5.2 | 1.3 | 4.7 | 1.2 | 1.4 | 4.5 | 1.7 | 4.8 | 4 | 1.6 | 4.5 | 1.2 | 1.6 | 4.4 | 2.9667 | 4.8 | 1.2
2026-05-04 | 07:00:00.000 | 7.5 | 6.2 | 7.8 | 7.7 | 8 | 7.9 | 7.7 | 7.9 | 7.9 | 8 | 8.1 | 8.1 | 7.7333 | 8.1 | 6.2 | 7.3 | 7.4 | 8.3 | 7.8 | 7.8 | 8 | 8.2 | 8.1 | 8.6 | 8 | 8.4 | 8.7 | 8.05 | 8.7 | 7.3 | 9 | 7.7 | 7.7 | 8.3 | 8.2 | 8.4 | 8.2 | 7.8 | 8 | 7.8 | 8.2 | 7.6 | 8.075 | 9 | 7.6
2026-05-04 | 07:15:00.000 | 35.1 | 0 | 37.1 | 36.9 | 37.7 | 36.6 | 36.5 | 35.7 | 36.4 | 36.5 | 37.9 | 37.2 | 36.6909 | 37.9 | 0 | 34.8 | 32.4 | 35.9 | 37 | 36.9 | 36.9 | 36.7 | 38.1 | 39.5 | 37.4 | 39.9 | 39.3 | 37.0667 | 39.9 | 32.4 | 37.1 | 33.7 | 35.2 | 36.6 | 36.1 | 37.4 | 36.9 | 36.4 | 35.9 | 34.4 | 37.7 | 34.4 | 35.9833 | 37.7 | 33.7
2026-05-04 | 07:30:00.000 | 68.6 | 20.2 | 70.9 | 70.6 | 71.5 | 70.4 | 69.7 | 70.1 | 70.9 | 70.9 | 72.6 | 71.4 | 66.4833 | 72.6 | 20.2 | 66.9 | 66.4 | 68.5 | 69.3 | 69 | 70.8 | 70 | 72 | 73.9 | 70.1 | 75 | 73.5 | 70.45 | 75 | 66.4 | 72.6 | 67.7 | 70 | 72.4 | 71.1 | 73.4 | 72.5 | 71.7 | 70.8 | 68.5 | 73.8 | 68.3 | 71.0667 | 73.8 | 67.7
2026-05-04 | 07:45:00.000 | 34.4 | 34.1 | 35.4 | 35.2 | 35.7 | 35.5 | 35.2 | 35.7 | 35.5 | 35.8 | 36.1 | 35.6 | 35.35 | 36.1 | 34.1 | 33.5 | 34.2 | 34.8 | 34.5 | 34.3 | 36.2 | 34.7 | 36.2 | 36.4 | 34.4 | 36.2 | 35.7 | 35.0917 | 36.4 | 33.5 | 34.2 | 33.9 | 32.8 | 35.1 | 34.8 | 35.2 | 35.6 | 33.7 | 34.7 | 34.1 | 35.9 | 32.4 | 34.3667 | 35.9 | 32.4
2026-05-04 | 08:00:00.000 | 83.7 | 81.9 | 76.3 | 81.2 | 80.4 | 80.4 | 79.6 | 87 | 84.7 | 83.2 | 85.1 | 81.6 | 82.0917 | 87 | 76.3 | 76.9 | 78.7 | 79.4 | 78.3 | 78.7 | 85 | 82.6 | 83.1 | 84.3 | 77 | 83.6 | 84.2 | 80.9833 | 85 | 76.9 | 93.5 | 92.4 | 99.1 | 104.1 | 107 | 106 | 104.8 | 101 | 98.2 | 95 | 90.7 | 95.6 | 98.95 | 107 | 90.7
2026-05-04 | 08:15:00.000 | 157.9 | 155.6 | 157.6 | 157.7 | 156.3 | 154.7 | 155.8 | 165.7 | 163.1 | 161.4 | 162.3 | 159.3 | 158.95 | 165.7 | 154.7 | 149.8 | 153.4 | 154.5 | 150.8 | 151.6 | 165 | 157.8 | 157.7 | 163 | 154.9 | 162.9 | 160.1 | 156.7917 | 165 | 149.8 | 170.3 | 167.6 | 170.6 | 180 | 175.2 | 183.8 | 171.5 | 174.8 | 167.8 | 170.8 | 172.8 | 162.1 | 172.275 | 183.8 | 162.1
2026-05-04 | 08:30:00.000 | 198 | 196.4 | 199.6 | 199.8 | 200.2 | 199.1 | 199.9 | 209.8 | 207 | 206.3 | 207.9 | 202.3 | 202.1917 | 209.8 | 196.4 | 190.7 | 197.1 | 196.9 | 193.3 | 193.7 | 210.4 | 200.7 | 207.7 | 208.7 | 199.6 | 208.9 | 205.4 | 201.0917 | 210.4 | 190.7 | 209.1 | 206.9 | 209.2 | 212.7 | 212.3 | 213.1 | 214.5 | 209.4 | 208.7 | 206.1 | 212.4 | 192.4 | 208.9 | 214.5 | 192.4
2026-05-04 | 08:45:00.000 | 239.4 | 238 | 238.1 | 242 | 237.1 | 231.5 | 236.5 | 251 | 245.3 | 246.9 | 246.6 | 228 | 240.0333 | 251 | 228 | 225.8 | 230.6 | 235.5 | 228.9 | 232.4 | 247 | 230.2 | 239.1 | 231.2 | 229.7 | 249.7 | 244 | 235.3417 | 249.7 | 225.8 | 243.8 | 254.4 | 253.1 | 260.2 | 260.8 | 259.9 | 252.3 | 255.6 | 254.2 | 252.4 | 259.9 | 229.9 | 253.0417 | 260.8 | 229.9
2026-05-04 | 09:00:00.000 | 271.6 | 259.3 | 268.8 | 262.1 | 267.8 | 268.4 | 273.4 | 274 | 271.7 | 265 | 272.6 | 271.8 | 268.875 | 274 | 259.3 | 260.7 | 268.9 | 268.3 | 263.8 | 267.2 | 267.6 | 271.4 | 273.5 | 275.8 | 271.7 | 278.4 | 277.4 | 270.3917 | 278.4 | 260.7 | 270.6 | 279.6 | 275.9 | 278.7 | 256 | 271.8 | 275.2 | 278.8 | 266.8 | 274.7 | 278.7 | 257.5 | 272.025 | 279.6 | 256
2026-05-04 | 09:15:00.000 | 268.9 | 268.3 | 266.2 | 270.5 | 268.5 | 268.2 | 269.8 | 271.9 | 271.9 | 269.6 | 269.5 | 270.7 | 269.5 | 271.9 | 266.2 | 264.6 | 259.5 | 268.1 | 265.3 | 266.3 | 270.2 | 268.2 | 270.7 | 260.7 | 269.4 | 271.4 | 272.3 | 267.225 | 272.3 | 259.5 | 270.9 | 270.1 | 269.9 | 269.6 | 269.4 | 259.2 | 270.8 | 270.3 | 271.3 | 270.7 | 270.5 | 265.5 | 269.0167 | 271.3 | 259.2
2026-05-04 | 09:30:00.000 | 280.5 | 280.3 | 280.4 | 281.3 | 280.5 | 281 | 281.6 | 281.4 | 281.6 | 281 | 281.3 | 280.5 | 280.95 | 281.6 | 280.3 | 279.4 | 280.4 | 280.2 | 279.6 | 280.4 | 281.3 | 280.1 | 281.3 | 281.3 | 281.1 | 281.2 | 281.2 | 280.625 | 281.3 | 279.4 | 281.4 | 280.7 | 281.2 | 281.2 | 281.2 | 281 | 280.6 | 270.8 | 270.7 | 280.9 | 280.9 | 279.6 | 279.1833 | 281.4 | 270.7
2026-05-04 | 09:45:00.000 | 281.4 | 281.3 | 281.4 | 281.9 | 281.6 | 281.7 | 271.7 | 281.4 | 281.7 | 281.7 | 281.5 | 281.2 | 280.7083 | 281.9 | 271.7 | 280.7 | 281.1 | 271.4 | 280.8 | 281.1 | 281.7 | 271.5 | 281.4 | 281.5 | 281.5 | 281.4 | 281.2 | 279.6083 | 281.7 | 271.4 | 281.8 | 281.2 | 281.5 | 281.5 | 281.8 | 281.2 | 281.3 | 281.1 | 281.2 | 281.4 | 281.4 | 281.7 | 281.425 | 281.8 | 281.1
2026-05-04 | 10:00:00.000 | 281.4 | 281.4 | 281.2 | 280.5 | 280.9 | 277.4 | 276 | 281.4 | 281.7 | 281.7 | 281.3 | 279.2 | 280.3417 | 281.7 | 276 | 276.9 | 281.2 | 277.9 | 281 | 281.8 | 281.4 | 278.5 | 281.1 | 281.4 | 280.5 | 278.6 | 281.2 | 280.125 | 281.8 | 276.9 | 281.8 | 281.2 | 281.4 | 281.5 | 281.7 | 281.2 | 281.3 | 281.1 | 261.5 | 281.3 | 281.4 | 281.8 | 279.7667 | 281.8 | 261.5
2026-05-04 | 10:15:00.000 | 281.4 | 281.4 | 281.1 | 281.1 | 281.4 | 281.1 | 281.4 | 281.4 | 281.7 | 281.7 | 281.3 | 281.2 | 281.35 | 281.7 | 281.1 | 281.1 | 281.5 | 281.8 | 281.1 | 281.6 | 281 | 281.4 | 281.1 | 281.4 | 281.2 | 271.1 | 256.3 | 278.3833 | 281.8 | 256.3 | 281.8 | 281.2 | 281.4 | 281.5 | 281.7 | 281.2 | 281.4 | 281.1 | 281.2 | 281.4 | 281.4 | 281.8 | 281.425 | 281.8 | 281.1
2026-05-04 | 10:30:00.000 | 280.5 | 281.5 | 281.1 | 281 | 281.4 | 281.1 | 281.4 | 281.4 | 281.7 | 281.7 | 281.3 | 281.2 | 281.275 | 281.7 | 280.5 | 281.2 | 281.5 | 281.8 | 281.2 | 281.6 | 281 | 281.4 | 281.1 | 281.4 | 281.2 | 257.3 | 250.1 | 276.7333 | 281.8 | 250.1 | 281.8 | 281.2 | 281.4 | 281 | 281.7 | 281.2 | 281.4 | 281.1 | 281.2 | 281.3 | 281.4 | 281.8 | 281.375 | 281.8 | 281
2026-05-04 | 10:45:00.000 | 276.1 | 276.5 | 280.4 | 281.6 | 281.4 | 281.1 | 281.4 | 279.8 | 281.7 | 281.7 | 271.3 | 281.2 | 279.5167 | 281.7 | 271.3 | 281.1 | 281.5 | 281.8 | 280.8 | 271.9 | 271 | 281.4 | 281.1 | 281.4 | 281.2 | 263.7 | 261.1 | 276.5 | 281.8 | 261.1 | 281.7 | 278.7 | 280.6 | 274.2 | 275 | 280.2 | 280.8 | 276.3 | 275 | 277.5 | 277.3 | 273.6 | 277.575 | 281.7 | 273.6
2026-05-04 | 11:00:00.000 | 281.8 | 280.8 | 281.2 | 281.2 | 281.2 | 281.2 | 281.4 | 281.3 | 281.7 | 281.5 | 281.2 | 281.2 | 281.3083 | 281.8 | 280.8 | 281.2 | 281.3 | 271.8 | 279.4 | 281.2 | 280.9 | 281.2 | 281.2 | 280.9 | 280.8 | 273.1 | 270.7 | 278.6417 | 281.3 | 270.7 | 281.2 | 281.3 | 281.4 | 280.9 | 281.3 | 281.1 | 270.5 | 281.6 | 281 | 281.3 | 281.2 | 281.3 | 280.3417 | 281.6 | 270.5
2026-05-04 | 11:15:00.000 | 279 | 280.9 | 281.4 | 271.3 | 281.4 | 281.3 | 281.4 | 281.4 | 281.7 | 281.7 | 281.3 | 281.2 | 280.3333 | 281.7 | 271.3 | 281.5 | 281.4 | 281.4 | 281.3 | 281.5 | 281 | 281.4 | 281.2 | 281.1 | 281.1 | 280.8 | 279.6 | 281.1083 | 281.5 | 279.6 | 281.4 | 281.3 | 281.5 | 281.2 | 281.4 | 281.2 | 280.8 | 281.6 | 281.1 | 281.5 | 281.2 | 281.4 | 281.3 | 281.6 | 280.8
2026-05-04 | 11:30:00.000 | 272 | 280.9 | 281.4 | 281.3 | 271.7 | 281.3 | 281.4 | 281.5 | 281.7 | 281.7 | 281.3 | 281.2 | 279.7833 | 281.7 | 271.7 | 281.3 | 281.4 | 281.4 | 271.2 | 281.5 | 281 | 281.4 | 281.2 | 281.2 | 281.1 | 281.5 | 281.3 | 280.4583 | 281.5 | 271.2 | 281.9 | 278.8 | 281.6 | 281 | 275.7 | 274.7 | 275 | 277 | 279.2 | 281.5 | 281.2 | 281.5 | 279.0917 | 281.9 | 274.7
2026-05-04 | 11:45:00.000 | 281.3 | 280.9 | 281.4 | 281.3 | 281.4 | 281.3 | 281.4 | 281.5 | 281.7 | 281.7 | 281.4 | 281.2 | 281.375 | 281.7 | 280.9 | 281.1 | 281.4 | 281.4 | 281.1 | 281.5 | 281 | 281.4 | 281.2 | 281.2 | 281.1 | 281.5 | 281 | 281.2417 | 281.5 | 281 | 282.2 | 281.1 | 281.7 | 280.6 | 281.3 | 281.1 | 281.3 | 281.1 | 281.2 | 281.5 | 281.3 | 281.4 | 281.3167 | 282.2 | 280.6
2026-05-04 | 12:00:00.000 | 281.3 | 280.8 | 281.4 | 281.3 | 281.4 | 281.3 | 281.4 | 281.5 | 281.7 | 281.7 | 281.3 | 281.2 | 281.3583 | 281.7 | 280.8 | 281.1 | 281.4 | 281.4 | 271.6 | 271.5 | 281 | 281.4 | 281.2 | 281.2 | 281.1 | 281.5 | 281 | 279.6167 | 281.5 | 271.5 | 282.1 | 281.1 | 281.7 | 270.6 | 281.3 | 271.1 | 281.3 | 281.1 | 281.2 | 281.5 | 261.3 | 281.4 | 277.975 | 282.1 | 261.3
2026-05-04 | 12:15:00.000 | 281.3 | 280.9 | 281.4 | 281.3 | 281.4 | 281.4 | 281.4 | 281.5 | 281.7 | 271.7 | 281.3 | 281.2 | 280.5417 | 281.7 | 271.7 | 281.2 | 281.4 | 281.4 | 281.3 | 271.5 | 281 | 281.4 | 281.2 | 281.2 | 281.1 | 281.5 | 281 | 280.4333 | 281.5 | 271.5 | 272.4 | 281.1 | 272.3 | 280.6 | 281.3 | 281.1 | 281.3 | 281.1 | 281.2 | 281.5 | 281.3 | 281.5 | 279.725 | 281.5 | 272.3
2026-05-04 | 12:30:00.000 | 281.3 | 280.9 | 281.4 | 280.8 | 281 | 281.4 | 281.4 | 281.5 | 281.7 | 281.7 | 281.4 | 281.1 | 281.3 | 281.7 | 280.8 | 281.1 | 281.4 | 281.4 | 281.3 | 281.5 | 281 | 271.7 | 281.2 | 281.2 | 271.1 | 281.5 | 281 | 279.6167 | 281.5 | 271.1 | 272.4 | 281.1 | 281.7 | 280.7 | 281.3 | 276.4 | 281.3 | 281.1 | 281.2 | 281.5 | 281.4 | 281.5 | 280.1333 | 281.7 | 272.4
2026-05-04 | 12:45:00.000 | 280.9 | 280.9 | 260.4 | 275.7 | 278.8 | 280 | 281.4 | 274.3 | 274.9 | 270.1 | 270.8 | 281.1 | 275.775 | 281.4 | 260.4 | 281.2 | 281.3 | 281.4 | 281.3 | 281.7 | 281 | 281.4 | 271.2 | 281.1 | 281.7 | 281.1 | 280.8 | 280.4333 | 281.7 | 271.2 | 276.9 | 275.8 | 275.4 | 275.2 | 277.6 | 264.3 | 281.3 | 270.9 | 281 | 279.3 | 275.6 | 281.5 | 276.2333 | 281.5 | 264.3
2026-05-04 | 13:00:00.000 | 281.2 | 281.4 | 281.4 | 280.9 | 281.4 | 281.4 | 281.4 | 271.6 | 281.1 | 281.3 | 281.1 | 281.7 | 280.4917 | 281.7 | 271.6 | 281.1 | 281.3 | 281.4 | 281.3 | 281.7 | 281 | 281.4 | 281.2 | 281.1 | 281.8 | 271 | 281 | 280.4417 | 281.8 | 271 | 281.1 | 281.6 | 270.3 | 260.7 | 281.4 | 270.9 | 281.3 | 281.2 | 281 | 281.3 | 281 | 271.4 | 276.9333 | 281.6 | 260.7
2026-05-04 | 13:15:00.000 | 281.2 | 281.4 | 281.4 | 280.9 | 281.4 | 281.4 | 281.4 | 281.7 | 281.1 | 281.2 | 281.1 | 281.7 | 281.325 | 281.7 | 280.9 | 281.2 | 281.4 | 281.4 | 281.3 | 281.7 | 281 | 281.3 | 281.2 | 281.2 | 281.8 | 281 | 281 | 281.2917 | 281.8 | 281 | 281.1 | 281.5 | 281.2 | 281.3 | 281.4 | 271.5 | 281.3 | 281.2 | 281 | 281.3 | 281 | 280.8 | 280.3833 | 281.5 | 271.5
2026-05-04 | 13:30:00.000 | 281.2 | 281.5 | 281.4 | 281 | 281.4 | 281.4 | 281.4 | 281.6 | 281.1 | 271.6 | 281.1 | 281.6 | 280.525 | 281.6 | 271.6 | 281.1 | 281.4 | 281.4 | 281.3 | 281.7 | 281 | 281.3 | 281.2 | 281.2 | 281.8 | 281 | 281 | 281.2833 | 281.8 | 281 | 281.1 | 281.5 | 281.1 | 271.6 | 281.4 | 281.5 | 281.3 | 281.2 | 281 | 281.3 | 281 | 281.3 | 280.4417 | 281.5 | 271.6
2026-05-04 | 13:45:00.000 | 281.2 | 281.5 | 281.4 | 281 | 281.4 | 281.4 | 281.4 | 281.7 | 281.1 | 281.3 | 281.1 | 281.7 | 281.35 | 281.7 | 281 | 281.1 | 281.3 | 281.4 | 281.3 | 281.7 | 281 | 281.4 | 281.2 | 281.2 | 272.4 | 281 | 281 | 280.5 | 281.7 | 272.4 | 281.1 | 281.5 | 281.2 | 281.4 | 281.4 | 281.5 | 281.4 | 281.2 | 281 | 281.3 | 281 | 281.2 | 281.2667 | 281.5 | 281
2026-05-04 | 14:00:00.000 | 281.2 | 280.8 | 280.8 | 281.1 | 281.6 | 280.6 | 281.3 | 281.6 | 281.2 | 281.3 | 281.1 | 281.4 | 281.1667 | 281.6 | 280.6 | 280.5 | 281.2 | 281.7 | 280.7 | 281.3 | 281.4 | 280.6 | 281.1 | 280.8 | 280.4 | 281 | 271.6 | 280.1917 | 281.7 | 271.6 | 281.1 | 281.7 | 281.2 | 281.5 | 281.4 | 281.5 | 280.9 | 281.3 | 280.9 | 281.3 | 271 | 281.1 | 280.4083 | 281.7 | 271
2026-05-04 | 14:15:00.000 | 272.2 | 281.2 | 281.2 | 281.6 | 281.3 | 280.8 | 281.5 | 281.7 | 281.1 | 270.9 | 281.5 | 281.6 | 279.7167 | 281.7 | 270.9 | 281.4 | 281.5 | 281.8 | 281.4 | 281.6 | 281.5 | 271.4 | 281 | 281.5 | 280.9 | 281.6 | 271.9 | 279.7917 | 281.8 | 271.4 | 270.4 | 281.9 | 271.1 | 281.4 | 281.4 | 271.3 | 280.6 | 281.5 | 280.8 | 281.3 | 281 | 281.8 | 278.7083 | 281.9 | 270.4
2026-05-04 | 14:30:00.000 | 281.9 | 271.1 | 281.5 | 281.4 | 281.2 | 281.7 | 281.6 | 271.7 | 281.3 | 281.2 | 271.7 | 281.6 | 278.9917 | 281.9 | 271.1 | 281.5 | 281.4 | 281.1 | 280.5 | 281.7 | 281.7 | 281.1 | 271.2 | 281.1 | 281.1 | 281.6 | 281.9 | 280.4917 | 281.9 | 271.2 | 281.1 | 269.7 | 281.2 | 281.5 | 281.4 | 281.5 | 270.6 | 281.5 | 280.9 | 271.1 | 281.1 | 281.7 | 278.6083 | 281.7 | 269.7
2026-05-04 | 14:45:00.000 | 281.7 | 280.9 | 281.5 | 281.2 | 281 | 281.4 | 281.4 | 281.7 | 281.2 | 281 | 281.4 | 281.5 | 281.325 | 281.7 | 280.9 | 281.1 | 281.2 | 280.9 | 280.6 | 271.6 | 271.6 | 281.4 | 281.2 | 281.4 | 281.8 | 281.6 | 281.9 | 279.6917 | 281.9 | 271.6 | 271.6 | 280.9 | 281 | 270.1 | 281.4 | 281.3 | 280.6 | 270.4 | 280.8 | 281.2 | 280.9 | 271.3 | 277.625 | 281.4 | 270.1
2026-05-04 | 15:00:00.000 | 281.9 | 281.1 | 281.5 | 281.4 | 271.2 | 281.5 | 281.6 | 281.8 | 281.2 | 281.2 | 271.4 | 281.7 | 279.7917 | 281.9 | 271.2 | 281.3 | 281.3 | 271.4 | 280.8 | 281.8 | 281.6 | 281.4 | 281.2 | 281.4 | 281.9 | 281.6 | 281.9 | 280.6333 | 281.9 | 271.4 | 260.8 | 281 | 270.3 | 281.6 | 271.7 | 251.7 | 280.6 | 281.5 | 280.9 | 281.4 | 281 | 281.8 | 275.3583 | 281.8 | 251.7
2026-05-04 | 15:15:00.000 | 281.9 | 271.7 | 281.5 | 281.4 | 281.2 | 281.5 | 281.6 | 281.7 | 281.2 | 281.2 | 281.4 | 281.6 | 280.6583 | 281.9 | 271.7 | 281.3 | 281.3 | 281.1 | 280.8 | 281.9 | 281.6 | 281.2 | 277.5 | 277.3 | 280.1 | 281.6 | 281.9 | 280.6333 | 281.9 | 277.3 | 281.1 | 281 | 281.3 | 281.6 | 281.4 | 281.5 | 280.6 | 281.5 | 280.9 | 281.5 | 271 | 281.8 | 280.4333 | 281.8 | 271
2026-05-04 | 15:30:00.000 | 271.8 | 281.1 | 281.5 | 281.4 | 281.1 | 271.5 | 281.6 | 281.7 | 281.2 | 281.2 | 262 | 281.6 | 278.1417 | 281.7 | 262 | 280.8 | 281.3 | 280.9 | 281 | 281.3 | 281.6 | 266.6 | 275.1 | 274.6 | 280.8 | 281.5 | 281.9 | 278.95 | 281.9 | 266.6 | 281.1 | 280.4 | 281.2 | 281.8 | 269.3 | 270.7 | 280.6 | 281.4 | 280.9 | 281.3 | 281 | 270.9 | 278.3833 | 281.8 | 269.3
2026-05-04 | 15:45:00.000 | 273.5 | 273.7 | 271.6 | 277.2 | 268.5 | 270.8 | 273.5 | 276.6 | 277.7 | 265.2 | 278.2 | 274.7 | 273.4333 | 278.2 | 265.2 | 264.8 | 251.6 | 268.5 | 268.4 | 266.9 | 270.4 | 242.3 | 253.8 | 260.4 | 277.5 | 275 | 271.5 | 264.2583 | 277.5 | 242.3 | 264.7 | 277 | 269.7 | 276.4 | 274.2 | 256.8 | 266.4 | 270.4 | 271.1 | 272.7 | 275.4 | 274.2 | 270.75 | 277 | 256.8
2026-05-04 | 16:00:00.000 | 268.5 | 273.5 | 276.6 | 271.1 | 274.2 | 273.3 | 272.3 | 276.4 | 274.3 | 276.3 | 274.4 | 275 | 273.825 | 276.6 | 268.5 | 271.3 | 273.9 | 270.9 | 272.5 | 272.7 | 276.1 | 233 | 246.2 | 271.4 | 271.4 | 265.2 | 274.4 | 266.5833 | 276.1 | 233 | 277.2 | 275.9 | 274.3 | 256.3 | 276.9 | 275.5 | 274.8 | 274.5 | 276 | 275.8 | 278.2 | 274.9 | 274.1917 | 278.2 | 256.3
2026-05-04 | 16:15:00.000 | 280 | 268.5 | 279.1 | 276.9 | 277.4 | 276 | 275.6 | 280.8 | 280.5 | 279.4 | 278.9 | 277.9 | 277.5833 | 280.8 | 268.5 | 273.7 | 273.8 | 277.2 | 271.8 | 264 | 278.7 | 226.8 | 262.6 | 279.1 | 278.8 | 278.3 | 278.7 | 270.2917 | 279.1 | 226.8 | 280.5 | 269.6 | 279.8 | 279 | 268.9 | 278.6 | 279.9 | 279.4 | 279.4 | 279.2 | 280.3 | 277.9 | 277.7083 | 280.5 | 268.9
2026-05-04 | 16:30:00.000 | 281.2 | 281.2 | 281.2 | 271.9 | 281.5 | 281.4 | 281.6 | 271.3 | 281.8 | 281.4 | 281.5 | 281 | 279.75 | 281.8 | 271.3 | 279.7 | 281.1 | 281.5 | 279.9 | 281.4 | 281.7 | 215.6 | 281.5 | 281.1 | 281.3 | 281.1 | 281.9 | 275.65 | 281.9 | 215.6 | 281.2 | 280.8 | 281.9 | 281.5 | 281.6 | 281.6 | 280.9 | 281.2 | 281.4 | 281.5 | 281.1 | 281.6 | 281.3583 | 281.9 | 280.8
2026-05-04 | 16:45:00.000 | 281.3 | 281.2 | 281.2 | 281.3 | 281.5 | 281.4 | 281.6 | 281.6 | 281.8 | 281.4 | 281.5 | 281 | 281.4 | 281.8 | 281 | 272.8 | 281.1 | 281.1 | 263.7 | 279.6 | 271.7 | 200.1 | 281.4 | 281.2 | 281.3 | 281 | 281.9 | 271.4083 | 281.9 | 200.1 | 281.2 | 280.9 | 282 | 281.4 | 281.6 | 281.5 | 280.9 | 281.2 | 281.4 | 281.5 | 281.1 | 280.3 | 281.25 | 282 | 280.3
2026-05-04 | 17:00:00.000 | 281.1 | 280.3 | 280.4 | 280.4 | 280.8 | 279.8 | 281 | 281.5 | 281.8 | 281.4 | 281 | 281 | 280.875 | 281.8 | 279.8 | 269 | 279.3 | 276.5 | 270.1 | 276.8 | 281.5 | 186.9 | 278.7 | 280.4 | 279.4 | 280.7 | 281.4 | 270.0583 | 281.5 | 186.9 | 281.2 | 280.9 | 281.9 | 281.4 | 271.9 | 271.2 | 280.9 | 281.2 | 281.4 | 281.5 | 281.1 | 276.9 | 279.2917 | 281.9 | 271.2
2026-05-04 | 17:15:00.000 | 243.1 | 240.2 | 238.5 | 236 | 238.8 | 236.2 | 237.9 | 255.9 | 245.1 | 246.4 | 247.1 | 232.5 | 241.475 | 255.9 | 232.5 | 226.3 | 234.3 | 224.5 | 216.5 | 231.6 | 243.9 | 216.3 | 238 | 241 | 232.1 | 240.5 | 241.8 | 232.2333 | 243.9 | 216.3 | 254.8 | 246.4 | 257.6 | 254.2 | 255 | 259.9 | 256.6 | 256.3 | 259.9 | 259.4 | 252.7 | 241.9 | 254.5583 | 259.9 | 241.9
2026-05-04 | 17:30:00.000 | 172.6 | 169.6 | 163.7 | 165.5 | 169.5 | 164.9 | 165 | 184.6 | 178.9 | 176 | 175.2 | 169.5 | 171.25 | 184.6 | 163.7 | 155.6 | 161.1 | 161.7 | 152.5 | 157.2 | 170 | 162.4 | 164.5 | 166.3 | 161.3 | 166.6 | 167.9 | 162.2583 | 170 | 152.5 | 192.4 | 183 | 191 | 186.3 | 182.4 | 188 | 195.3 | 191.7 | 192.5 | 180.3 | 191.3 | 174.9 | 187.425 | 195.3 | 174.9
2026-05-04 | 17:45:00.000 | 130.8 | 129.2 | 128.4 | 127.2 | 127 | 123.4 | 123.4 | 145.3 | 141 | 133.9 | 136.7 | 127.7 | 131.1667 | 145.3 | 123.4 | 117.1 | 122 | 118.9 | 116.8 | 117.6 | 132.7 | 122.9 | 121.5 | 127.7 | 123 | 123.8 | 124.5 | 122.375 | 132.7 | 116.8 | 146.2 | 133.9 | 142 | 140.7 | 138 | 141.3 | 143.3 | 131.8 | 142.6 | 142.2 | 145.9 | 127.6 | 139.625 | 146.2 | 127.6
2026-05-04 | 18:00:00.000 | 71.6 | 70.3 | 69.5 | 69.3 | 68.6 | 68.6 | 67.8 | 75.6 | 74.5 | 73.2 | 72.6 | 70.4 | 71 | 75.6 | 67.8 | 64.3 | 67 | 66.4 | 63.1 | 64.1 | 71.3 | 67.6 | 69.8 | 69.8 | 65.3 | 69.2 | 70 | 67.325 | 71.3 | 63.1 | 78.5 | 76.7 | 76.4 | 75.7 | 75 | 75.4 | 77.8 | 76 | 77.3 | 77.8 | 78.3 | 70.7 | 76.3 | 78.5 | 70.7
2026-05-04 | 18:15:00.000 | 39.1 | 38.6 | 39 | 39.3 | 39.1 | 38.9 | 38.8 | 41.1 | 40.7 | 40.3 | 40.2 | 39.5 | 39.55 | 41.1 | 38.6 | 37.2 | 38.8 | 38.3 | 37.3 | 37.4 | 41 | 39.2 | 40.7 | 40.8 | 39 | 41 | 41.2 | 39.325 | 41.2 | 37.2 | 41.1 | 40.2 | 40.5 | 40.6 | 40.6 | 40.7 | 41.1 | 40.2 | 40.4 | 40.1 | 41 | 37.3 | 40.3167 | 41.1 | 37.3
2026-05-04 | 18:30:00.000 | 28.8 | 28.4 | 28.7 | 28.9 | 28.8 | 28.7 | 28.6 | 30.2 | 29.9 | 29.7 | 29.6 | 27.9 | 29.0167 | 30.2 | 27.9 | 27.4 | 28.6 | 28.3 | 27.5 | 27.5 | 30.2 | 28.9 | 30 | 30.1 | 27.6 | 30.3 | 30.4 | 28.9 | 30.4 | 27.4 | 30.2 | 28.4 | 29.8 | 29.8 | 29.7 | 29.8 | 30 | 29.4 | 29.6 | 29.3 | 30.1 | 27.2 | 29.4417 | 30.2 | 27.2
2026-05-04 | 18:45:00.000 | 22.3 | 22 | 22.3 | 22.5 | 22.4 | 22.4 | 22.4 | 23.5 | 23.3 | 23.1 | 23 | 22.6 | 22.65 | 23.5 | 22 | 21.3 | 22.3 | 22.1 | 21.4 | 21.4 | 23.3 | 22.3 | 23.1 | 23.2 | 22.2 | 23.3 | 23.4 | 22.4417 | 23.4 | 21.3 | 23.6 | 23.1 | 23.2 | 23.2 | 23.1 | 23 | 23.3 | 22.9 | 23.1 | 22.1 | 23.5 | 21.1 | 22.9333 | 23.6 | 21.1
2026-05-04 | 19:00:00.000 | 18.3 | 18 | 17.6 | 18.4 | 18.2 | 18.2 | 18 | 19 | 18.8 | 18.7 | 18.6 | 18.2 | 18.3333 | 19 | 17.6 | 17.2 | 17.9 | 17.7 | 17.2 | 17.2 | 18.9 | 18.1 | 18.6 | 18.7 | 17.8 | 18.8 | 18.8 | 18.075 | 18.9 | 17.2 | 19 | 18.5 | 18.8 | 18.8 | 18.8 | 18.8 | 19 | 18.7 | 18.8 | 18.1 | 19 | 17.4 | 18.6417 | 19 | 17.4
2026-05-04 | 19:15:00.000 | 6.8 | 6.7 | 6.8 | 6.9 | 6.8 | 6.9 | 6.8 | 7.2 | 7.2 | 7.1 | 7.1 | 6.9 | 6.9333 | 7.2 | 6.7 | 6.3 | 6.6 | 6.5 | 6.4 | 6 | 7 | 6.8 | 7 | 7 | 6.7 | 7 | 7.1 | 6.7 | 7.1 | 6 | 7.3 | 7 | 7.2 | 7.2 | 7.3 | 7.2 | 7.3 | 6.5 | 7 | 7.2 | 7.3 | 6.7 | 7.1 | 7.3 | 6.5
2026-05-04 | 19:30:00.000 | 5.7 | 5.6 | 5.2 | 5.9 | 5.8 | 6 | 6.1 | 6.4 | 6.4 | 6.4 | 6.3 | 6.2 | 6 | 6.4 | 5.2 | 5.5 | 5.9 | 5.6 | 5.5 | 5.5 | 6.1 | 5.8 | 6.2 | 6.2 | 5.9 | 6.2 | 6.3 | 5.8917 | 6.3 | 5.5 | 6.7 | 6.5 | 6.6 | 6.5 | 6.1 | 5.9 | 6.3 | 6.3 | 6.5 | 6.7 | 6.6 | 5.6 | 6.3583 | 6.7 | 5.6
2026-05-04 | 19:45:00.000 | 9.5 | 9.4 | 9.5 | 9.7 | 9.6 | 9.7 | 9.5 | 10.1 | 10 | 9.9 | 9.9 | 9.6 | 9.7 | 10.1 | 9.4 | 9.3 | 9.8 | 9.5 | 9.2 | 9.2 | 10.2 | 9.7 | 10.3 | 10.3 | 9.9 | 10 | 10.5 | 9.825 | 10.5 | 9.2 | 10.2 | 10.1 | 10.1 | 10 | 10 | 9.8 | 9.9 | 9.8 | 10.1 | 10.3 | 10.2 | 8.7 | 9.9333 | 10.3 | 8.7
2026-05-04 | 20:00:00.000 | 2.9 | 2.8 | 2.9 | 3 | 2.9 | 3.1 | 2.9 | 3.1 | 3.1 | 3.1 | 3.1 | 2.9 | 2.9833 | 3.1 | 2.8 | 2.7 | 2.9 | 2.8 | 2.7 | 2.7 | 3 | 3 | 3 | 3.1 | 2.9 | 3.1 | 3.1 | 2.9167 | 3.1 | 2.7 | 3.1 | 2.9 | 3.1 | 3 | 3.1 | 3 | 3 | 3 | 3.1 | 3.1 | 3.1 | 2.8 | 3.025 | 3.1 | 2.8
2026-05-04 | 20:15:00.000 | 0.2 | 0.1 | 0.3 | 0.3 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.2 | 0.5 | 0.325 | 0.5 | 0.1 | 0.3 | 0.4 | 0.3 | 0.4 | 0.8 | 0.4 | 0.5 | 0.7 | 0.5 | 0.4 | 0.3 | 0.8 | 0.48333 | 0.8 | 0.3 | 0.6 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.475 | 0.6 | 0.4
2026-05-04 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.14167 | 0.5 | 0.1 | 0.1 | 0.1 | 0.7 | 0.1 | 0.5 | 0.1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.6 | 0.24167 | 0.7 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.4 | 0.1
2026-05-04 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.2 | 0 | 0 | 0 | 0.3 | 0 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.2 | 0
2026-05-04 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0
2026-05-04 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320