## PR_Calc
PR CALCULATION
05 MAGGIO 2026 | [67 empty] | 5 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 48
RAW PR | [64 empty] | 0.87095 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 87.095
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 87.1428
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 87.095
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-05 | 00:00:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9197.1
2026-05-05 | 00:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 00:30:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 00:45:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 02:15:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 02:30:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 03:15:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 03:30:00.000 | -1 | -0.00025 | -0.6 | -0.00015 | -0.0002 | 0 | -0.0002 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 03:45:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 04:00:00.000 | -0.7 | -0.000175 | -0.3 | -7.5e-05 | -0.000125 | 0 | -0.000125 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 04:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 04:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 04:45:00.000 | -1 | -0.00025 | -0.7 | -0.000175 | -0.0002125 | 0 | -0.0002125 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 05:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 05:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 05:30:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 05:45:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 06:00:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 06:15:00.000 | 1.8 | 0.00045 | 2.1 | 0.000525 | 0.0004875 | 0 | 0.0004875 | 0.15385 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 06:30:00.000 | 13.7 | 0.003425 | 13.8 | 0.00345 | 0.0034375 | 0 | 0.0034375 | 0.0072727 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 06:45:00.000 | 30.2 | 0.00755 | 30.5 | 0.007625 | 0.0075875 | 0 | 0.0075875 | 0.0098847 | 30386.2 | 30386.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 07:00:00.000 | 62.1 | 0.015525 | 63.4 | 0.01585 | 0.015688 | 62.75 | 0.01585 | 0.020717 | 30386.2 | 30386.4 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 07:15:00.000 | 119.3 | 0.029825 | 119.4 | 0.02985 | 0.029838 | 119.35 | 0.02985 | 0.00083787 | 30386.4 | 30386.6 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 07:30:00.000 | 73.4 | 0.01835 | 72 | 0.018 | 0.018175 | 72.7 | 0.01835 | 0.019257 | 30386.6 | 30386.9 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 07:45:00.000 | 28.7 | 0.007175 | 28.5 | 0.007125 | 0.00715 | 0 | 0.00715 | 0.006993 | 30386.9 | 30387.1 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 08:00:00.000 | 29 | 0.00725 | 29.1 | 0.007275 | 0.0072625 | 0 | 0.0072625 | 0.0034423 | 30387.1 | 30387.2 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 08:15:00.000 | 57.3 | 0.014325 | 57.2 | 0.0143 | 0.014312 | 57.25 | 0.014325 | 0.0017467 | 30387.2 | 30387.3 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 08:30:00.000 | 97.2 | 0.0243 | 96.6 | 0.02415 | 0.024225 | 96.9 | 0.0243 | 0.006192 | 30387.3 | 30387.5 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 08:45:00.000 | 116.8 | 0.0292 | 115.7 | 0.028925 | 0.029062 | 116.25 | 0.0292 | 0.0094624 | 30387.5 | 30387.9 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 09:00:00.000 | 120.1 | 0.030025 | 116.2 | 0.02905 | 0.029538 | 118.15 | 0.030025 | 0.033009 | 30387.9 | 30388.3 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 09:15:00.000 | 284.7 | 0.071175 | 286.7 | 0.071675 | 0.071425 | 285.7 | 0.071675 | 0.0070004 | 30388.3 | 30388.9 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 09:30:00.000 | 854.3 | 0.21357 | 849.6 | 0.2124 | 0.21299 | 851.95 | 0.21357 | 0.0055168 | 30388.9 | 30390.6 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 09:45:00.000 | 411.7 | 0.10293 | 389.6 | 0.0974 | 0.10016 | 400.65 | 0.10293 | 0.05516 | 30390.6 | 30392.6 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 10:00:00.000 | 758.6 | 0.18965 | 724.9 | 0.18122 | 0.18544 | 741.75 | 0.18965 | 0.045433 | 30392.6 | 30393.9 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 10:15:00.000 | 941.5 | 0.23538 | 958.7 | 0.23967 | 0.23752 | 950.1 | 0.23967 | 0.018103 | 30393.9 | 30396.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 10:30:00.000 | 924.7 | 0.23118 | 912.1 | 0.22803 | 0.2296 | 918.4 | 0.23118 | 0.01372 | 30396.2 | 30398.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 10:45:00.000 | 946.9 | 0.23672 | 928.8 | 0.2322 | 0.23446 | 937.85 | 0.23672 | 0.019299 | 30398.6 | 30401.1 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 11:00:00.000 | 823.2 | 0.2058 | 823.4 | 0.20585 | 0.20583 | 823.3 | 0.20585 | 0.00024292 | 30401.1 | 30403.5 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 11:15:00.000 | 932.7 | 0.23318 | 916.3 | 0.22908 | 0.23113 | 924.5 | 0.23318 | 0.017739 | 30403.5 | 30405.8 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 11:30:00.000 | 923.3 | 0.23083 | 898.9 | 0.22473 | 0.22778 | 911.1 | 0.23083 | 0.026781 | 30405.8 | 30408.3 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 11:45:00.000 | 868.7 | 0.21718 | 860.3 | 0.21507 | 0.21613 | 864.5 | 0.21718 | 0.0097166 | 30408.3 | 30410.7 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 12:00:00.000 | 904.5 | 0.22612 | 918.4 | 0.2296 | 0.22786 | 911.45 | 0.2296 | 0.01525 | 30410.7 | 30413.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 12:15:00.000 | 834.3 | 0.20857 | 826.2 | 0.20655 | 0.20756 | 830.25 | 0.20857 | 0.0097561 | 30413.1 | 30415.3 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 12:30:00.000 | 827.5 | 0.20688 | 790.8 | 0.1977 | 0.20229 | 809.15 | 0.20688 | 0.045356 | 30415.3 | 30417.7 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 12:45:00.000 | 913 | 0.22825 | 907.1 | 0.22678 | 0.22751 | 910.05 | 0.22825 | 0.0064832 | 30417.7 | 30419.9 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 13:00:00.000 | 874.6 | 0.21865 | 858.7 | 0.21468 | 0.21666 | 866.65 | 0.21865 | 0.018347 | 30419.9 | 30422.3 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 13:15:00.000 | 914.6 | 0.22865 | 893 | 0.22325 | 0.22595 | 903.8 | 0.22865 | 0.023899 | 30422.3 | 30424.7 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 13:30:00.000 | 929.9 | 0.23247 | 912.6 | 0.22815 | 0.23031 | 921.25 | 0.23247 | 0.018779 | 30424.7 | 30427.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 13:45:00.000 | 962.5 | 0.24063 | 941.3 | 0.23532 | 0.23797 | 951.9 | 0.24063 | 0.022271 | 30427.2 | 30429.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 14:00:00.000 | 954.8 | 0.2387 | 930.8 | 0.2327 | 0.2357 | 942.8 | 0.2387 | 0.025456 | 30429.6 | 30432.1 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 14:15:00.000 | 981.3 | 0.24532 | 965.1 | 0.24128 | 0.2433 | 973.2 | 0.24532 | 0.016646 | 30432.1 | 30434.6 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 14:30:00.000 | 882.4 | 0.2206 | 866.9 | 0.21673 | 0.21866 | 874.65 | 0.2206 | 0.017721 | 30434.6 | 30437 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 14:45:00.000 | 969 | 0.24225 | 951.1 | 0.23778 | 0.24001 | 960.05 | 0.24225 | 0.018645 | 30437 | 30439.4 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 15:00:00.000 | 948.5 | 0.23713 | 927.5 | 0.23187 | 0.2345 | 938 | 0.23713 | 0.022388 | 30439.4 | 30441.9 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 15:15:00.000 | 941.5 | 0.23538 | 919.8 | 0.22995 | 0.23266 | 930.65 | 0.23538 | 0.023317 | 30441.9 | 30444.4 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 15:30:00.000 | 937.4 | 0.23435 | 914 | 0.2285 | 0.23142 | 925.7 | 0.23435 | 0.025278 | 30444.4 | 30446.9 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 15:45:00.000 | 944.5 | 0.23613 | 921.5 | 0.23037 | 0.23325 | 933 | 0.23613 | 0.024652 | 30446.9 | 30449.3 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 16:00:00.000 | 936.7 | 0.23418 | 914.3 | 0.22858 | 0.23137 | 925.5 | 0.23418 | 0.024203 | 30449.3 | 30451.8 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 16:15:00.000 | 942.8 | 0.2357 | 919.9 | 0.22997 | 0.23284 | 931.35 | 0.2357 | 0.024588 | 30451.8 | 30454.2 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 16:30:00.000 | 684.3 | 0.17107 | 677.9 | 0.16947 | 0.17027 | 681.1 | 0.17107 | 0.0093966 | 30454.2 | 30456.5 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 16:45:00.000 | 655 | 0.16375 | 635.9 | 0.15898 | 0.16136 | 645.45 | 0.16375 | 0.029592 | 30456.5 | 30458 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 17:00:00.000 | 751.4 | 0.18785 | 719.6 | 0.1799 | 0.18388 | 735.5 | 0.18785 | 0.043236 | 30458 | 30460 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 17:15:00.000 | 797.6 | 0.1994 | 798.5 | 0.19962 | 0.19951 | 798.05 | 0.19962 | 0.0011277 | 30460 | 30462.1 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 17:30:00.000 | 580.2 | 0.14505 | 596.9 | 0.14922 | 0.14714 | 588.55 | 0.14922 | 0.028375 | 30462.1 | 30464.1 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 17:45:00.000 | 227.9 | 0.056975 | 223.6 | 0.0559 | 0.056438 | 225.75 | 0.056975 | 0.019048 | 30464.1 | 30465.2 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 18:00:00.000 | 180.9 | 0.045225 | 174.3 | 0.043575 | 0.0444 | 177.6 | 0.045225 | 0.037162 | 30465.2 | 30465.8 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 18:15:00.000 | 150.2 | 0.03755 | 146.7 | 0.036675 | 0.037112 | 148.45 | 0.03755 | 0.023577 | 30465.8 | 30466.3 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 18:30:00.000 | 146.9 | 0.036725 | 146.9 | 0.036725 | 0.036725 | 146.9 | 0.036725 | 0 | 30466.3 | 30466.7 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 18:45:00.000 | 100.2 | 0.02505 | 101.2 | 0.0253 | 0.025175 | 100.7 | 0.0253 | 0.0099305 | 30466.7 | 30467.1 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 19:00:00.000 | 85.6 | 0.0214 | 89.9 | 0.022475 | 0.021937 | 87.75 | 0.022475 | 0.049003 | 30467.1 | 30467.3 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 19:15:00.000 | 67.3 | 0.016825 | 70.2 | 0.01755 | 0.017188 | 68.75 | 0.01755 | 0.042182 | 30467.3 | 30467.6 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 19:30:00.000 | 43.4 | 0.01085 | 45.6 | 0.0114 | 0.011125 | 0 | 0.011125 | 0.049438 | 30467.6 | 30467.7 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 19:45:00.000 | 17.5 | 0.004375 | 17.8 | 0.00445 | 0.0044125 | 0 | 0.0044125 | 0.016997 | 30467.7 | 30467.8 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 20:00:00.000 | 4.9 | 0.001225 | 5.1 | 0.001275 | 0.00125 | 0 | 0.00125 | 0.04 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 20:15:00.000 | 0.1 | 2.5e-05 | 0.1 | 2.5e-05 | 2.5e-05 | 0 | 2.5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 20:30:00.000 | -0.9 | -0.000225 | 0 | 0 | -0.0001125 | 0 | -0.0001125 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 20:45:00.000 | -0.9 | -0.000225 | 0 | 0 | -0.0001125 | 0 | -0.0001125 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 21:30:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 22:00:00.000 | -0.8 | -0.0002 | 0 | 0 | -0.0001 | 0 | -0.0001 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 22:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 22:30:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 22:45:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 23:00:00.000 | -0.9 | -0.000225 | 0 | 0 | -0.0001125 | 0 | -0.0001125 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 23:15:00.000 | -0.8 | -0.0002 | 0 | 0 | -0.0001 | 0 | -0.0001 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 23:30:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
2026-05-05 | 23:45:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0142
PR for each inverter |  |  | 7.6226 |  | 7.5042 | 7.5634 |  | 7.6402 |  |  |  | 81600 |  | 0.88896 | 0.88272 | 0.88449 | 0.88905 | 0.88614 | 0.88344 | 0.8903 | 0.86407 | 0.86067 | 0.85693 | 0.85863 | 0.89065 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.88763 | 0.8717 | 0.87992 | 0.89645 | 0.90232 | 0.85026 | 0.8801 | 0.85376 | 0.85525 | 0.8855 | 0.85847 | 0.85815 |  |  |  | 0 | 0.8596 | 0.85708 | 0.85674 | 0.85886 | 0.86022 | 0.85858 | 0.86134 | 0.8551 | 0.86001 | 0.8584 | 0.85537 | 0.91453 | #DIV/0! | #DIV/0! | #DIV/0! | 0 |  | 0.87143 |  | #DIV/0! | #DIV/0! | 8.8964e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-05 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 06:30:00.000 | 0.2 | 0.4 | 0.7 | 0.4 | 2.6 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.3 | 1 | 0.64167 | 2.6 | 0.2 | 0.5 | 0.4 | 2.2 | 0.4 | 2.1 | 0.6 | 0.5 | 3.5 | 0.6 | 0.3 | 0.1 | 2.1 | 1.1083 | 3.5 | 0.1 | 2.9 | 0.4 | 1.1 | 0.6 | 0.6 | 0.3 | 0.4 | 0.2 | 0.5 | 0.3 | 0.4 | 0.6 | 0.69167 | 2.9 | 0.2
2026-05-05 | 06:45:00.000 | 8.4 | 8.2 | 8.4 | 8.7 | 8.4 | 8.4 | 8.4 | 8.8 | 8.8 | 8.7 | 8.6 | 8.5 | 8.525 | 8.8 | 8.2 | 7.9 | 8.3 | 8.2 | 7.9 | 8 | 8.6 | 8.5 | 9 | 8.8 | 8 | 8.8 | 8.9 | 8.4083 | 9 | 7.9 | 9.1 | 8.7 | 8.8 | 8.1 | 8.7 | 8.8 | 8.9 | 8.7 | 8.6 | 8.8 | 8.8 | 8 | 8.6667 | 9.1 | 8
2026-05-05 | 07:00:00.000 | 19.5 | 19.3 | 19.6 | 19.9 | 19.7 | 19.6 | 18.9 | 20.7 | 20.6 | 20.4 | 20.4 | 20.1 | 19.8917 | 20.7 | 18.9 | 18.7 | 19.6 | 19.4 | 17.9 | 18.8 | 20.9 | 20.1 | 20.7 | 20.8 | 19.9 | 20.9 | 21.1 | 19.9 | 21.1 | 17.9 | 20.8 | 20.5 | 20.7 | 20.1 | 20.7 | 19.7 | 20.8 | 20.4 | 20.5 | 20.4 | 20.9 | 18.8 | 20.3583 | 20.9 | 18.8
2026-05-05 | 07:15:00.000 | 38.5 | 38.2 | 38.8 | 39.2 | 38.9 | 38.6 | 38.7 | 40.5 | 40.2 | 40 | 40.2 | 38 | 39.15 | 40.5 | 38 | 36.9 | 38.3 | 38.1 | 37.2 | 37.2 | 40.7 | 39.2 | 40.5 | 40.6 | 38.8 | 40.8 | 41.1 | 39.1167 | 41.1 | 36.9 | 40.7 | 39.9 | 40.3 | 40.6 | 40.4 | 40.7 | 40.9 | 40 | 40.1 | 39.7 | 40.9 | 37.2 | 40.1167 | 40.9 | 37.2
2026-05-05 | 07:30:00.000 | 24.9 | 24.6 | 24.1 | 25 | 24.8 | 24.6 | 24.6 | 25.8 | 25.4 | 25.2 | 25.2 | 24.7 | 24.9083 | 25.8 | 24.1 | 23.2 | 24.1 | 23.9 | 23.3 | 23.2 | 25.3 | 24.3 | 24.9 | 25 | 23.8 | 24.9 | 25 | 24.2417 | 25.3 | 23.2 | 25.7 | 25.3 | 25.6 | 25.7 | 25.6 | 25.6 | 26 | 25.5 | 25.6 | 25.4 | 25.9 | 24 | 25.4917 | 26 | 24
2026-05-05 | 07:45:00.000 | 9.8 | 9.6 | 9.7 | 9.8 | 9.7 | 9.7 | 9.7 | 10.1 | 10 | 9.9 | 9.9 | 9.7 | 9.8 | 10.1 | 9.6 | 9.1 | 9.5 | 9.5 | 9.1 | 8.8 | 9.9 | 9.6 | 9.8 | 9.8 | 9.3 | 9.7 | 9.8 | 9.4917 | 9.9 | 8.8 | 9.6 | 9.9 | 10 | 10 | 10 | 9.9 | 10.1 | 9.9 | 10 | 9.9 | 10.1 | 9.3 | 9.8917 | 10.1 | 9.3
2026-05-05 | 08:00:00.000 | 9.9 | 9.7 | 9.9 | 10.1 | 10 | 10 | 10.1 | 10.4 | 10.3 | 10 | 10.2 | 10.1 | 10.0583 | 10.4 | 9.7 | 9.5 | 10.1 | 10 | 9.5 | 9.5 | 10.4 | 10.1 | 10.3 | 10.3 | 9.8 | 10.2 | 10.4 | 10.0083 | 10.4 | 9.5 | 10.1 | 10.3 | 10.3 | 10.2 | 10.2 | 10 | 10.1 | 10 | 10.1 | 10.2 | 10.3 | 9.2 | 10.0833 | 10.3 | 9.2
2026-05-05 | 08:15:00.000 | 19.7 | 19.5 | 19.7 | 20.2 | 20 | 20 | 20.3 | 21.1 | 20.8 | 20.7 | 20.7 | 20.5 | 20.2667 | 21.1 | 19.5 | 19.2 | 20.4 | 20.1 | 19.2 | 19.4 | 21.1 | 20.3 | 21 | 20.9 | 20 | 20.9 | 21.3 | 20.3167 | 21.3 | 19.2 | 20.8 | 20.8 | 20.6 | 20.4 | 20.3 | 19.9 | 20.1 | 19.8 | 20.2 | 20.4 | 20.5 | 18.1 | 20.1583 | 20.8 | 18.1
2026-05-05 | 08:30:00.000 | 33.8 | 33.4 | 33.7 | 34.4 | 34 | 33.9 | 34.5 | 35.9 | 35.5 | 35.1 | 35 | 34.6 | 34.4833 | 35.9 | 33.4 | 32.6 | 34.5 | 33.9 | 32.5 | 32.6 | 35.6 | 34.2 | 35.4 | 35.2 | 33.7 | 33.9 | 35.6 | 34.1417 | 35.6 | 32.5 | 35.3 | 35.4 | 35.1 | 34.9 | 34.8 | 34.3 | 34.8 | 34.1 | 34.6 | 33.5 | 35.1 | 31.6 | 34.4583 | 35.4 | 31.6
2026-05-05 | 08:45:00.000 | 41.2 | 40.5 | 40.9 | 41.6 | 41.1 | 40.9 | 41.6 | 43.7 | 42.9 | 42.4 | 42.3 | 41.8 | 41.7417 | 43.7 | 40.5 | 39.3 | 41.4 | 39.3 | 39 | 39.1 | 43 | 41.2 | 42.6 | 42.2 | 40.3 | 42.1 | 42.6 | 41.0083 | 43 | 39 | 42.4 | 42.7 | 42.4 | 40.9 | 42.2 | 41.8 | 42.6 | 41.5 | 42 | 42.2 | 42.4 | 38.9 | 41.8333 | 42.7 | 38.9
2026-05-05 | 09:00:00.000 | 43.1 | 42.4 | 42.8 | 43.7 | 43.4 | 43.2 | 44.1 | 45.9 | 45 | 44.5 | 44.4 | 44 | 43.875 | 45.9 | 42.4 | 42.1 | 43.9 | 43.3 | 41.4 | 41.7 | 45.5 | 43.4 | 44.9 | 44.5 | 42.6 | 44.4 | 45 | 43.5583 | 45.5 | 41.4 | 44.4 | 44.4 | 44 | 43.9 | 43.7 | 43.1 | 44.1 | 41.4 | 43.4 | 43.7 | 44.1 | 40.2 | 43.3667 | 44.4 | 40.2
2026-05-05 | 09:15:00.000 | 93.1 | 91.8 | 95.6 | 96.7 | 98 | 97.1 | 100 | 107.3 | 102.7 | 104.3 | 104.4 | 100.1 | 99.2583 | 107.3 | 91.8 | 95 | 99 | 97.4 | 93.6 | 93.6 | 103.7 | 100.9 | 101.7 | 103.2 | 99.3 | 102.4 | 103.2 | 99.4167 | 103.7 | 93.6 | 103 | 96.7 | 100.8 | 101.2 | 93.7 | 101.4 | 102.2 | 101.3 | 103 | 102.6 | 103.7 | 87.2 | 99.7333 | 103.7 | 87.2
2026-05-05 | 09:30:00.000 | 270.6 | 268.5 | 269.9 | 274.3 | 271.8 | 273.9 | 273.2 | 277.7 | 275.4 | 274.1 | 275.6 | 273 | 273.1667 | 277.7 | 268.5 | 267.7 | 274 | 273.5 | 267 | 268.7 | 263.1 | 233.8 | 273.8 | 274 | 271.1 | 274.4 | 272.8 | 267.825 | 274.4 | 233.8 | 262.6 | 274.1 | 271.9 | 274.5 | 270.7 | 271.5 | 275.6 | 272.5 | 274.8 | 272.8 | 275.9 | 243 | 269.9917 | 275.9 | 243
2026-05-05 | 09:45:00.000 | 139.1 | 137.6 | 139.9 | 138.3 | 138.3 | 139.2 | 125.5 | 147.9 | 142.8 | 140.8 | 142.5 | 133.5 | 138.7833 | 147.9 | 125.5 | 134.9 | 140.1 | 134.1 | 132.5 | 131.9 | 115.4 | 120.1 | 134 | 134.4 | 130.5 | 132.8 | 125.9 | 130.55 | 140.1 | 115.4 | 138.8 | 140.6 | 139.3 | 140.9 | 141.8 | 132.7 | 146.2 | 136.5 | 137 | 140.5 | 139 | 138 | 139.275 | 146.2 | 132.7
2026-05-05 | 10:00:00.000 | 218.9 | 219.2 | 218.6 | 226.8 | 220.5 | 222.7 | 231.2 | 223.4 | 221.6 | 222.1 | 222.8 | 219.8 | 222.3 | 231.2 | 218.6 | 220.8 | 224.4 | 227.3 | 223.2 | 222.1 | 199.3 | 202 | 224.7 | 213.5 | 218.2 | 221.9 | 223.7 | 218.425 | 227.3 | 199.3 | 217.7 | 218.8 | 212.7 | 216.1 | 214.5 | 212.9 | 216.7 | 212.9 | 217 | 207.1 | 210.4 | 209.9 | 213.8917 | 218.8 | 207.1
2026-05-05 | 10:15:00.000 | 273.5 | 270.9 | 276.4 | 268.8 | 273.4 | 272.2 | 273.4 | 276.7 | 275.6 | 279.4 | 275.5 | 281.6 | 274.7833 | 281.6 | 268.8 | 275.9 | 276.1 | 274.9 | 274.5 | 276.7 | 251.6 | 263.8 | 279.8 | 280.3 | 280.9 | 280.9 | 281.7 | 274.7583 | 281.7 | 251.6 | 281.5 | 281.2 | 281.3 | 281 | 281.5 | 281.5 | 281.4 | 271.7 | 281.5 | 281.7 | 279.5 | 274.4 | 279.85 | 281.7 | 271.7
2026-05-05 | 10:30:00.000 | 281.2 | 281.3 | 281 | 281.1 | 281.2 | 280.9 | 281.5 | 281.9 | 281.5 | 281.4 | 281.4 | 281.1 | 281.2917 | 281.9 | 280.9 | 279.6 | 281.4 | 281.4 | 278.3 | 257.3 | 280.7 | 281.1 | 271.9 | 281.4 | 281.1 | 281.2 | 281.9 | 278.1083 | 281.9 | 257.3 | 281.7 | 281.4 | 281.5 | 281.7 | 281.4 | 280.9 | 281.6 | 281.1 | 281.3 | 281.6 | 281.5 | 280.4 | 281.3417 | 281.7 | 280.4
2026-05-05 | 10:45:00.000 | 280.6 | 281.2 | 280.3 | 280.6 | 281.1 | 280.7 | 281.3 | 281.9 | 281.5 | 281.6 | 281.2 | 280.9 | 281.075 | 281.9 | 280.3 | 278.7 | 281.2 | 281.2 | 256.8 | 247.3 | 281.5 | 281.8 | 281.1 | 281.2 | 281.2 | 281.2 | 272.5 | 275.475 | 281.8 | 247.3 | 281.6 | 281.3 | 281.3 | 281.4 | 281 | 261.4 | 281.6 | 280.6 | 281.4 | 281.5 | 271.7 | 280.4 | 278.7667 | 281.6 | 261.4
2026-05-05 | 11:00:00.000 | 245.1 | 244.6 | 240.2 | 251.2 | 250.8 | 248.4 | 253.7 | 263.6 | 247.8 | 244.1 | 264.2 | 254.2 | 250.6583 | 264.2 | 240.2 | 239.7 | 249.3 | 248.3 | 216.3 | 213.8 | 256.9 | 250.2 | 248.1 | 256.8 | 251.6 | 256.7 | 256.9 | 245.3833 | 256.9 | 213.8 | 249.4 | 264.3 | 251.5 | 264 | 269.9 | 256.6 | 260.5 | 251.9 | 253.5 | 263.4 | 262.6 | 253.7 | 258.4417 | 269.9 | 249.4
2026-05-05 | 11:15:00.000 | 281 | 281.6 | 281 | 281.5 | 281.9 | 281.6 | 281.4 | 281.9 | 281.2 | 281.7 | 281.4 | 281.2 | 281.45 | 281.9 | 281 | 279.7 | 281.5 | 281.2 | 254.2 | 254.6 | 280.8 | 282.1 | 281 | 282 | 281.4 | 281.9 | 281.4 | 276.8167 | 282.1 | 254.2 | 271.8 | 281.7 | 281.2 | 281.2 | 281.2 | 281 | 281.2 | 281.4 | 281.6 | 281.8 | 281.6 | 281 | 280.5583 | 281.8 | 271.8
2026-05-05 | 11:30:00.000 | 279.1 | 278.2 | 276.6 | 279.2 | 276.7 | 277.9 | 276.2 | 279.1 | 279.6 | 278.2 | 278.1 | 277.2 | 278.0083 | 279.6 | 276.2 | 272.8 | 277.6 | 275.9 | 254.9 | 255.4 | 277.7 | 278.8 | 277.2 | 277.3 | 277.5 | 277.9 | 277.7 | 273.3917 | 278.8 | 254.9 | 280.5 | 277 | 277.3 | 276.3 | 279.2 | 278.9 | 279.3 | 276.8 | 276.5 | 276.9 | 270.8 | 275.7 | 277.1 | 280.5 | 270.8
2026-05-05 | 11:45:00.000 | 265.6 | 262.8 | 265.2 | 265.1 | 254.6 | 253.2 | 257.1 | 270.1 | 267.3 | 269.2 | 268.1 | 266.5 | 263.7333 | 270.1 | 253.2 | 255.7 | 262.8 | 243.6 | 243.5 | 244.4 | 268.8 | 264.4 | 269.4 | 269 | 263.6 | 267.8 | 268.9 | 260.1583 | 269.4 | 243.5 | 273.8 | 265 | 273.6 | 274.9 | 275.9 | 275 | 273.3 | 260.1 | 270.4 | 270.7 | 262.8 | 260.7 | 269.6833 | 275.9 | 260.1
2026-05-05 | 12:00:00.000 | 267.8 | 265.7 | 264.5 | 255.8 | 264.7 | 264.4 | 265.6 | 266.1 | 271.9 | 266.2 | 271.4 | 270.3 | 266.2 | 271.9 | 255.8 | 255.2 | 268.6 | 270.1 | 257.7 | 261.7 | 271.5 | 268.9 | 272.6 | 262.3 | 264.2 | 271.1 | 270.1 | 266.1667 | 272.6 | 255.2 | 269.9 | 275.6 | 271.4 | 272.4 | 275.7 | 276.1 | 272.6 | 270.7 | 262.8 | 273.6 | 271.1 | 260.4 | 271.025 | 276.1 | 260.4
2026-05-05 | 12:15:00.000 | 248.1 | 247.7 | 246.8 | 248 | 248.5 | 250.7 | 248.3 | 260.1 | 256.4 | 260.9 | 247.5 | 248.5 | 250.9583 | 260.9 | 246.8 | 247.2 | 252 | 248.8 | 241.1 | 232.9 | 249.3 | 254.8 | 248.8 | 252 | 251.4 | 257 | 251.5 | 248.9 | 257 | 232.9 | 247.2 | 255.1 | 244.7 | 249.5 | 261.9 | 261.4 | 259.9 | 256.6 | 256.8 | 256.7 | 260.4 | 242.6 | 254.4 | 261.9 | 242.6
2026-05-05 | 12:30:00.000 | 262.6 | 249.5 | 249.2 | 254 | 259.5 | 261.2 | 263.5 | 267 | 266 | 263.2 | 262.9 | 253.7 | 259.3583 | 267 | 249.2 | 252.3 | 261 | 259 | 249 | 252.6 | 255.3 | 258.2 | 260.6 | 262.5 | 256 | 261.3 | 261.9 | 257.475 | 262.5 | 249 | 260.9 | 257 | 260.9 | 240.5 | 260.4 | 247.1 | 261 | 260.3 | 261.5 | 260.6 | 262.1 | 250.7 | 256.9167 | 262.1 | 240.5
2026-05-05 | 12:45:00.000 | 263.6 | 261.3 | 261.7 | 264.1 | 254.4 | 262.7 | 264.3 | 264.9 | 266.2 | 266.2 | 264.6 | 265.7 | 263.3083 | 266.2 | 254.4 | 261.3 | 263.9 | 262.7 | 257.2 | 261.4 | 267.3 | 265.5 | 266.1 | 266.5 | 264.7 | 267.4 | 268.1 | 264.3417 | 268.1 | 257.2 | 270.1 | 269.1 | 267.9 | 268.4 | 260.1 | 268.6 | 268.2 | 266.8 | 265.9 | 266.1 | 268.6 | 258.2 | 266.5 | 270.1 | 258.2
2026-05-05 | 13:00:00.000 | 266.4 | 263.2 | 260.4 | 265.2 | 261.1 | 258.7 | 264.8 | 268.5 | 268.3 | 258 | 265.3 | 264.8 | 263.725 | 268.5 | 258 | 255.6 | 258.7 | 259.2 | 251.1 | 254.9 | 270.4 | 263.2 | 255.2 | 266.7 | 260.3 | 267.1 | 259.1 | 260.125 | 270.4 | 251.1 | 252.3 | 260.3 | 273.7 | 260.9 | 271.7 | 271.9 | 273 | 261 | 271.3 | 271.8 | 271.5 | 248 | 265.6167 | 273.7 | 248
2026-05-05 | 13:15:00.000 | 277.9 | 277.7 | 278.7 | 278.7 | 279.1 | 279 | 279.3 | 271.7 | 279.7 | 273.9 | 279.9 | 278.8 | 277.8667 | 279.9 | 271.7 | 272.9 | 267.7 | 278.1 | 275 | 274.8 | 278.6 | 278.3 | 280 | 269.5 | 278 | 280.3 | 280.1 | 276.1083 | 280.3 | 267.7 | 281.1 | 281.2 | 270.7 | 280.9 | 280.9 | 280.5 | 280.9 | 280.5 | 279.3 | 278.3 | 280.8 | 275 | 279.175 | 281.2 | 270.7
2026-05-05 | 13:30:00.000 | 274.1 | 263.1 | 265 | 271.5 | 275 | 274.6 | 271.3 | 276.1 | 273.9 | 270.7 | 276.5 | 263.9 | 271.3083 | 276.5 | 263.1 | 273.5 | 274.8 | 273.1 | 274.6 | 274.5 | 277 | 273.8 | 274.7 | 274 | 273.4 | 274.9 | 275.2 | 274.4583 | 277 | 273.1 | 276.6 | 278.5 | 278.5 | 279.3 | 269.6 | 278.4 | 276.4 | 268 | 275.9 | 265.8 | 276.7 | 273.8 | 274.7917 | 279.3 | 265.8
2026-05-05 | 13:45:00.000 | 281.5 | 281.5 | 281.3 | 281.1 | 281.5 | 281.8 | 281.5 | 281.1 | 281.2 | 281 | 282 | 281.4 | 281.4083 | 282 | 281 | 281.5 | 281.4 | 282 | 281.6 | 281.9 | 281.1 | 281.7 | 281.4 | 281.2 | 281.9 | 280.9 | 281.4 | 281.5 | 282 | 280.9 | 281.4 | 281.1 | 281.1 | 281.2 | 281.3 | 271.1 | 273.8 | 281.2 | 281.2 | 280.8 | 281.2 | 281.5 | 279.7417 | 281.5 | 271.1
2026-05-05 | 14:00:00.000 | 279.2 | 279.5 | 277.7 | 278.1 | 268.2 | 260.2 | 277.4 | 281.3 | 278.7 | 272.9 | 279.7 | 276.1 | 275.75 | 281.3 | 260.2 | 271.9 | 276 | 276.2 | 275.8 | 262.2 | 279.4 | 278.5 | 277.7 | 279.9 | 278.8 | 279.4 | 277.9 | 276.1417 | 279.9 | 262.2 | 280.2 | 269.2 | 277.2 | 280.1 | 269.6 | 279.9 | 275.3 | 280.1 | 280.4 | 279.1 | 274.5 | 280.2 | 277.15 | 280.4 | 269.2
2026-05-05 | 14:15:00.000 | 281.5 | 272.2 | 281.1 | 281.5 | 281.3 | 281 | 281.2 | 281.1 | 281.3 | 281.3 | 281.1 | 281.3 | 280.4917 | 281.5 | 272.2 | 280.7 | 281.5 | 281.1 | 281.4 | 280.5 | 281.7 | 281.7 | 281.3 | 281.3 | 280.9 | 282.1 | 281.2 | 281.2833 | 282.1 | 280.5 | 281.5 | 281.7 | 281.3 | 281.4 | 281.1 | 280.9 | 281.4 | 281.1 | 281.2 | 277.8 | 281.2 | 281.3 | 280.9917 | 281.7 | 277.8
2026-05-05 | 14:30:00.000 | 265.2 | 264.1 | 265.4 | 265 | 264.9 | 264.4 | 264.8 | 251.3 | 258.4 | 268.3 | 268.1 | 265.8 | 263.8083 | 268.3 | 251.3 | 254.2 | 261.4 | 260.5 | 260 | 262.5 | 269.2 | 265.7 | 260.6 | 261.5 | 264.7 | 269.1 | 269.4 | 263.2333 | 269.4 | 254.2 | 271.1 | 261.1 | 270.5 | 270 | 269.4 | 269.1 | 261.3 | 269.7 | 269.9 | 262.6 | 261.3 | 252.1 | 265.675 | 271.1 | 252.1
2026-05-05 | 14:45:00.000 | 281.1 | 281 | 281.6 | 281.9 | 281.4 | 280.9 | 281.7 | 281.2 | 281.3 | 281.8 | 271.5 | 281.6 | 280.5833 | 281.9 | 271.5 | 274.4 | 281.1 | 282 | 271.5 | 281.2 | 281.5 | 281 | 281.6 | 281.5 | 281.4 | 281.1 | 281.3 | 279.9667 | 282 | 271.5 | 273.2 | 281.9 | 281.1 | 281.4 | 271.5 | 281.3 | 281.7 | 281.4 | 281.7 | 281.5 | 281.1 | 280.9 | 279.8917 | 281.9 | 271.5
2026-05-05 | 15:00:00.000 | 281.3 | 280.9 | 281 | 281.9 | 281.4 | 280.9 | 281.7 | 281.2 | 281.4 | 281.8 | 281.1 | 271 | 280.4667 | 281.9 | 271 | 260.5 | 275.6 | 281.9 | 280 | 281.1 | 281.2 | 281.2 | 281.6 | 281.3 | 271.8 | 271.5 | 281.3 | 277.4167 | 281.9 | 260.5 | 271.7 | 271.6 | 281.2 | 271.8 | 281.6 | 281.3 | 281.8 | 281.5 | 281.8 | 281.4 | 280.8 | 281.7 | 279.0167 | 281.8 | 271.6
2026-05-05 | 15:15:00.000 | 280.4 | 280.1 | 281.3 | 281.3 | 281.4 | 280.6 | 281.5 | 281.2 | 280.6 | 281.4 | 281.2 | 280.9 | 280.9917 | 281.5 | 280.1 | 249.3 | 265.5 | 281.1 | 275.1 | 280.8 | 280.6 | 281.2 | 281.1 | 281.2 | 281.5 | 281.3 | 281.7 | 276.7 | 281.7 | 249.3 | 281.7 | 281.4 | 280.7 | 271.5 | 281.4 | 281.1 | 281.3 | 281.5 | 281.4 | 280.7 | 280.9 | 280.2 | 280.3167 | 281.7 | 271.5
2026-05-05 | 15:30:00.000 | 281.2 | 280.9 | 281.5 | 281.4 | 281.3 | 282.2 | 281.2 | 281.1 | 281.1 | 281 | 281.3 | 281.7 | 281.325 | 282.2 | 280.9 | 239.9 | 256.2 | 279.2 | 271.9 | 280.2 | 281 | 281 | 281.2 | 281 | 281.4 | 281.2 | 281.6 | 274.65 | 281.6 | 239.9 | 281.6 | 281.1 | 281.5 | 281.1 | 281.3 | 281.1 | 280.7 | 281 | 281.2 | 270.9 | 280.9 | 279.7 | 280.175 | 281.6 | 270.9
2026-05-05 | 15:45:00.000 | 281.5 | 281.2 | 281.5 | 281.6 | 281.5 | 272.7 | 281.5 | 281.1 | 281.1 | 281.2 | 281.2 | 281.9 | 280.6667 | 281.9 | 272.7 | 234.2 | 248.6 | 277.3 | 270.3 | 280.5 | 271.7 | 281.2 | 281.2 | 281.2 | 281.4 | 281.5 | 272.1 | 271.7667 | 281.5 | 234.2 | 281.6 | 281.3 | 281.5 | 281.2 | 281.6 | 281 | 280.9 | 281.2 | 281.2 | 281.1 | 271.2 | 280.3 | 280.3417 | 281.6 | 271.2
2026-05-05 | 16:00:00.000 | 281.4 | 280.7 | 281.2 | 281.5 | 281.3 | 281 | 281.4 | 281.1 | 281.1 | 281.2 | 281.2 | 281.9 | 281.25 | 281.9 | 280.7 | 223.2 | 237.1 | 262 | 265.3 | 276.8 | 281 | 280.4 | 281.2 | 281.2 | 280.7 | 281.5 | 281.8 | 269.35 | 281.8 | 223.2 | 281.6 | 281.2 | 281.7 | 281.2 | 281.5 | 281 | 280.9 | 281.2 | 281.2 | 281.1 | 281.1 | 276.5 | 280.85 | 281.7 | 276.5
2026-05-05 | 16:15:00.000 | 280.7 | 280 | 280 | 280.5 | 280 | 280.1 | 281 | 281.1 | 281.1 | 281.2 | 281.2 | 281.4 | 280.6917 | 281.4 | 280 | 225.6 | 238.9 | 271.6 | 265.4 | 277.1 | 281 | 279.7 | 281.2 | 281.2 | 280.1 | 281.5 | 281.8 | 270.425 | 281.8 | 225.6 | 281.6 | 281.3 | 281.5 | 281.2 | 281 | 281 | 280.9 | 281.2 | 281.2 | 281.1 | 281.1 | 276.1 | 280.7667 | 281.6 | 276.1
2026-05-05 | 16:30:00.000 | 204.7 | 201.9 | 203.9 | 201.2 | 199.7 | 200.8 | 197.3 | 212.4 | 212.3 | 212.7 | 208.1 | 207.9 | 205.2417 | 212.7 | 197.3 | 190.9 | 198.3 | 194.3 | 191.1 | 197.7 | 206.2 | 201.3 | 210.5 | 212.9 | 207 | 210.6 | 211.2 | 202.6667 | 212.9 | 190.9 | 210.3 | 213.7 | 208.7 | 220.4 | 213.9 | 219.2 | 207.8 | 206.5 | 209 | 206.2 | 199.6 | 204.2 | 209.9583 | 220.4 | 199.6
2026-05-05 | 16:45:00.000 | 186.6 | 190.9 | 193.6 | 192.9 | 193.6 | 192.8 | 194.3 | 200.7 | 198.8 | 199.4 | 198.5 | 195.2 | 194.775 | 200.7 | 186.6 | 186.9 | 195 | 186.9 | 189.9 | 194.7 | 198.7 | 194.2 | 196.7 | 197.5 | 194.7 | 205.7 | 206.6 | 195.625 | 206.6 | 186.9 | 207.4 | 195.7 | 192.5 | 197.5 | 197 | 197.4 | 187 | 197.5 | 196.1 | 194.8 | 189.1 | 184 | 194.6667 | 207.4 | 184
2026-05-05 | 17:00:00.000 | 231.2 | 228.1 | 224.8 | 231 | 226.2 | 227.5 | 234.4 | 234.2 | 233.1 | 223.6 | 229.1 | 233.5 | 229.725 | 234.4 | 223.6 | 215 | 225.6 | 223.3 | 217.6 | 221.7 | 231.4 | 224.1 | 227.7 | 233.7 | 228.7 | 238 | 241.7 | 227.375 | 241.7 | 215 | 234.7 | 225.7 | 218.1 | 231.6 | 229.4 | 230.9 | 234.4 | 227.5 | 232.2 | 234.2 | 208 | 221 | 227.3083 | 234.7 | 208
2026-05-05 | 17:15:00.000 | 240.9 | 238.4 | 238.5 | 238 | 238.4 | 236.7 | 240.2 | 255.4 | 252.5 | 249 | 247.5 | 239.5 | 242.9167 | 255.4 | 236.7 | 224.9 | 235.1 | 232.4 | 225.4 | 231 | 245.7 | 232.7 | 239.7 | 242.4 | 233.1 | 243.4 | 245.4 | 235.9333 | 245.7 | 224.9 | 259.6 | 253.7 | 251.2 | 256.3 | 254.6 | 256.1 | 259.6 | 252.3 | 254.4 | 254.7 | 254.1 | 237.1 | 253.6417 | 259.6 | 237.1
2026-05-05 | 17:30:00.000 | 184.7 | 186.7 | 182.4 | 187.3 | 184.6 | 172.9 | 189.5 | 194.6 | 192.9 | 189.1 | 187.7 | 184.7 | 186.425 | 194.6 | 172.9 | 175.1 | 181.1 | 181.4 | 171.3 | 176.8 | 185.9 | 173.9 | 181.6 | 180.6 | 171.4 | 176.2 | 180.3 | 177.9667 | 185.9 | 171.3 | 197.1 | 180 | 187.6 | 190.3 | 190.8 | 193.4 | 183.1 | 194.9 | 189.8 | 197.6 | 198.3 | 183.3 | 190.5167 | 198.3 | 180
2026-05-05 | 17:45:00.000 | 74.3 | 73.5 | 73.9 | 74.2 | 74.5 | 73.8 | 74 | 78.1 | 77.3 | 76.3 | 75.8 | 74.8 | 75.0417 | 78.1 | 73.5 | 70.6 | 73.7 | 72.9 | 71.1 | 72.1 | 76.6 | 73 | 75.9 | 76.1 | 73.2 | 76.8 | 77.2 | 74.1 | 77.2 | 70.6 | 78.1 | 76.1 | 76 | 76.1 | 75.6 | 76.2 | 77.5 | 75.7 | 76.4 | 76.2 | 77.8 | 69.9 | 75.9667 | 78.1 | 69.9
2026-05-05 | 18:00:00.000 | 59.9 | 59.1 | 59.4 | 59.8 | 59.7 | 59 | 59 | 62.5 | 61.7 | 61 | 60.7 | 59.7 | 60.125 | 62.5 | 59 | 56.8 | 59.1 | 58.6 | 57.1 | 57.6 | 62.1 | 59.3 | 61.6 | 61.7 | 59.3 | 62.3 | 62.6 | 59.8417 | 62.6 | 56.8 | 62.3 | 60.8 | 60.9 | 61.1 | 60.9 | 61.4 | 62.3 | 60.8 | 61.1 | 60.4 | 62.2 | 57.1 | 60.9417 | 62.3 | 57.1
2026-05-05 | 18:15:00.000 | 49.7 | 49.1 | 49.3 | 49.6 | 49.6 | 49.2 | 49.3 | 52.2 | 51.6 | 51 | 50.7 | 49.9 | 50.1 | 52.2 | 49.1 | 47.2 | 49.3 | 48.9 | 47.6 | 48.1 | 51.5 | 49.2 | 51.1 | 51.3 | 49.3 | 51.6 | 51.9 | 49.75 | 51.9 | 47.2 | 52.6 | 51.2 | 51.2 | 51.3 | 51 | 51.2 | 51.9 | 50.8 | 51.1 | 50.8 | 52.2 | 47.2 | 51.0417 | 52.6 | 47.2
2026-05-05 | 18:30:00.000 | 48.7 | 48.3 | 48.3 | 48.9 | 48.8 | 48.4 | 48.9 | 51.7 | 51.1 | 50.6 | 50.2 | 49.3 | 49.4333 | 51.7 | 48.3 | 46.4 | 48.7 | 48.1 | 46.5 | 47 | 50.2 | 47.8 | 49.6 | 49.6 | 47.4 | 49.5 | 49.7 | 48.375 | 50.2 | 46.4 | 51.8 | 51 | 50.5 | 50.6 | 50.1 | 50 | 51.1 | 49.9 | 50.6 | 50.7 | 51.7 | 46.5 | 50.375 | 51.8 | 46.5
2026-05-05 | 18:45:00.000 | 32.8 | 32.4 | 32.6 | 32.9 | 32.7 | 32.6 | 32.9 | 34.8 | 34.4 | 34 | 33.8 | 33.2 | 33.2583 | 34.8 | 32.4 | 31.1 | 32.6 | 32.1 | 31.1 | 31.3 | 33.9 | 32.3 | 32.4 | 33.4 | 31.9 | 33.3 | 33.5 | 32.4083 | 33.9 | 31.1 | 35 | 34.5 | 34.5 | 34.5 | 34.4 | 34.3 | 34.8 | 34.1 | 34.5 | 34.5 | 35 | 31.8 | 34.325 | 35 | 31.8
2026-05-05 | 19:00:00.000 | 27.9 | 27.7 | 27.8 | 28.2 | 28 | 28 | 28.6 | 30.3 | 30 | 29.6 | 29.4 | 28.9 | 28.7 | 30.3 | 27.7 | 26.6 | 28.2 | 27.6 | 26.5 | 26.7 | 29 | 27.7 | 28.6 | 28.5 | 27.2 | 28.2 | 28.5 | 27.775 | 29 | 26.5 | 30.7 | 30.6 | 30.4 | 30.3 | 30.1 | 29.7 | 30.1 | 29.6 | 30.2 | 30.6 | 30.6 | 27.4 | 30.025 | 30.7 | 27.4
2026-05-05 | 19:15:00.000 | 22 | 21.8 | 21.9 | 22.3 | 22.1 | 22.2 | 22.6 | 23.8 | 23.5 | 23.2 | 23.1 | 22.7 | 22.6 | 23.8 | 21.8 | 21 | 22.2 | 21.8 | 20.9 | 21 | 22.8 | 21.7 | 22.4 | 22.3 | 21.2 | 21.9 | 22.2 | 21.7833 | 22.8 | 20.9 | 24.1 | 24 | 23.1 | 23.8 | 23.7 | 23.2 | 23.6 | 23.2 | 23.7 | 24.1 | 24 | 21.5 | 23.5 | 24.1 | 21.5
2026-05-05 | 19:30:00.000 | 14.1 | 13.9 | 14.1 | 14.3 | 14.2 | 14.3 | 14.4 | 15.2 | 15.1 | 14.9 | 14.8 | 14.6 | 14.4917 | 15.2 | 13.9 | 13.4 | 14.2 | 13.9 | 13.4 | 13.4 | 14.7 | 14 | 14.5 | 14.5 | 13.8 | 14 | 14.5 | 14.025 | 14.7 | 13.4 | 15.4 | 15.3 | 15.4 | 15.3 | 15.2 | 14.9 | 15.1 | 14.9 | 15.3 | 15.5 | 15.5 | 13.8 | 15.1333 | 15.5 | 13.8
2026-05-05 | 19:45:00.000 | 5.5 | 5.4 | 5.5 | 5.6 | 5.5 | 5.7 | 5.6 | 5.8 | 5.8 | 5.8 | 5.7 | 5.6 | 5.625 | 5.8 | 5.4 | 5.2 | 5.5 | 5.5 | 5.3 | 5.3 | 5.8 | 5.6 | 5.8 | 5.9 | 5.5 | 5.9 | 5.9 | 5.6 | 5.9 | 5.2 | 5.9 | 5.7 | 5.9 | 5.8 | 5.8 | 5.7 | 5.7 | 5.7 | 5.9 | 5.9 | 5.9 | 5.3 | 5.7667 | 5.9 | 5.3
2026-05-05 | 20:00:00.000 | 1.6 | 1.3 | 1.6 | 1.7 | 1.5 | 1.7 | 1.7 | 1.7 | 1.8 | 1.8 | 1.7 | 1.6 | 1.6417 | 1.8 | 1.3 | 1.6 | 1.6 | 1.4 | 1.6 | 1.5 | 1.7 | 1.7 | 1.5 | 1.8 | 1.7 | 1.7 | 1.6 | 1.6167 | 1.8 | 1.4 | 1.6 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7 | 1.6 | 1.7 | 1.8 | 1.8 | 1.8 | 1.5 | 1.6833 | 1.8 | 1.5
2026-05-05 | 20:15:00.000 | 0.1 | 0.1 | 0.2 | 0.3 | 0.4 | 0.2 | 0.3 | 0.3 | 0.4 | 0.2 | 0.1 | 0.5 | 0.25833 | 0.5 | 0.1 | 0.2 | 0.3 | 0.7 | 0.3 | 0.6 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.1 | 0.5 | 0.375 | 0.7 | 0.1 | 0.8 | 0.5 | 0.4 | 0.3 | 0.4 | 0.4 | 0.3 | 0.4 | 0.3 | 0.4 | 0.5 | 0.3 | 0.41667 | 0.8 | 0.3
2026-05-05 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.15833 | 0.7 | 0.1 | 0.1 | 0.1 | 0.7 | 0.1 | 0.4 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.9 | 0.29167 | 0.9 | 0.1 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13333 | 0.5 | 0.1
2026-05-05 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0.3 | 0 | 0.2 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.275 | 0.4 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0
2026-05-05 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.125 | 0.2 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0
2026-05-05 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-05 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320