## PR_Calc
PR CALCULATION
06 MAGGIO 2026 | [67 empty] | 6 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 49
RAW PR | [64 empty] | 1.0013 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 100.1348
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 100.1549
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 100.1348
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-06 | 00:00:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3907.8
2026-05-06 | 00:15:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 01:15:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 01:30:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 01:45:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 02:30:00.000 | -0.3 | -7.5e-05 | 0 | 0 | -3.75e-05 | 0 | -3.75e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 02:45:00.000 | -0.7 | -0.000175 | 0 | 0 | -8.75e-05 | 0 | -8.75e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 03:00:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 03:30:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 03:45:00.000 | -0.9 | -0.000225 | -0.5 | -0.000125 | -0.000175 | 0 | -0.000175 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 04:15:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 04:30:00.000 | -0.8 | -0.0002 | 0 | 0 | -0.0001 | 0 | -0.0001 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 04:45:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 05:15:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 05:30:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 05:45:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 06:15:00.000 | 0.4 | 0.0001 | 0.6 | 0.00015 | 0.000125 | 0 | 0.000125 | 0.4 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 06:30:00.000 | 5.2 | 0.0013 | 5.3 | 0.001325 | 0.0013125 | 0 | 0.0013125 | 0.019048 | 30467.8 | 30467.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 06:45:00.000 | 15.4 | 0.00385 | 15.4 | 0.00385 | 0.00385 | 0 | 0.00385 | 0 | 30467.8 | 30467.9 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 07:00:00.000 | 37.8 | 0.00945 | 37.9 | 0.009475 | 0.0094625 | 0 | 0.0094625 | 0.002642 | 30467.9 | 30467.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 07:15:00.000 | 105.3 | 0.026325 | 104.8 | 0.0262 | 0.026262 | 105.05 | 0.026325 | 0.0047596 | 30467.9 | 30468.1 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 07:30:00.000 | 126.1 | 0.031525 | 126.7 | 0.031675 | 0.0316 | 126.4 | 0.031675 | 0.0047468 | 30468.1 | 30468.5 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 07:45:00.000 | 118.1 | 0.029525 | 118.5 | 0.029625 | 0.029575 | 118.3 | 0.029625 | 0.0033812 | 30468.5 | 30468.8 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 08:00:00.000 | 126.1 | 0.031525 | 125.9 | 0.031475 | 0.0315 | 126 | 0.031525 | 0.0015873 | 30468.8 | 30469.2 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 08:15:00.000 | 133.3 | 0.033325 | 133.7 | 0.033425 | 0.033375 | 133.5 | 0.033425 | 0.0029963 | 30469.2 | 30469.6 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 08:30:00.000 | 138.9 | 0.034725 | 138.9 | 0.034725 | 0.034725 | 138.9 | 0.034725 | 0 | 30469.6 | 30470 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 08:45:00.000 | 140.7 | 0.035175 | 139 | 0.03475 | 0.034963 | 139.85 | 0.035175 | 0.012156 | 30470 | 30470.4 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 09:00:00.000 | 208.2 | 0.05205 | 199.5 | 0.049875 | 0.050963 | 203.85 | 0.05205 | 0.042678 | 30470.4 | 30471 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 09:15:00.000 | 179.2 | 0.0448 | 183.4 | 0.04585 | 0.045325 | 181.3 | 0.04585 | 0.023166 | 30471 | 30471.7 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 09:30:00.000 | 165.1 | 0.041275 | 169.3 | 0.042325 | 0.0418 | 167.2 | 0.042325 | 0.02512 | 30471.7 | 30472.2 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 09:45:00.000 | 262.5 | 0.065625 | 267.3 | 0.066825 | 0.066225 | 264.9 | 0.066825 | 0.01812 | 30472.2 | 30472.9 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 10:00:00.000 | 379.8 | 0.09495 | 389.1 | 0.097275 | 0.096113 | 384.45 | 0.097275 | 0.02419 | 30472.9 | 30474 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 10:15:00.000 | 367.8 | 0.09195 | 359 | 0.08975 | 0.09085 | 363.4 | 0.09195 | 0.024216 | 30474 | 30475.2 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 10:30:00.000 | 371 | 0.09275 | 371.3 | 0.092825 | 0.092787 | 371.15 | 0.092825 | 0.0008083 | 30475.2 | 30476.3 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 10:45:00.000 | 634.3 | 0.15857 | 621.8 | 0.15545 | 0.15701 | 628.05 | 0.15857 | 0.019903 | 30476.3 | 30477.7 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 11:00:00.000 | 667.3 | 0.16683 | 660 | 0.165 | 0.16591 | 663.65 | 0.16683 | 0.011 | 30477.7 | 30479.9 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 11:15:00.000 | 310.6 | 0.07765 | 313.1 | 0.078275 | 0.077963 | 311.85 | 0.078275 | 0.0080167 | 30479.9 | 30481.2 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 11:30:00.000 | 397.7 | 0.099425 | 403.7 | 0.10093 | 0.10018 | 400.7 | 0.10093 | 0.014974 | 30481.2 | 30482.2 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 11:45:00.000 | 514.4 | 0.1286 | 517.4 | 0.12935 | 0.12898 | 515.9 | 0.12935 | 0.0058151 | 30482.2 | 30483.8 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 12:00:00.000 | 373.7 | 0.093425 | 375.4 | 0.09385 | 0.093637 | 374.55 | 0.09385 | 0.0045388 | 30483.8 | 30485.2 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 12:15:00.000 | 269.9 | 0.067475 | 267.7 | 0.066925 | 0.0672 | 268.8 | 0.067475 | 0.0081845 | 30485.2 | 30486.1 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 12:30:00.000 | 199.7 | 0.049925 | 197.2 | 0.0493 | 0.049612 | 198.45 | 0.049925 | 0.012598 | 30486.1 | 30486.9 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 12:45:00.000 | 172.8 | 0.0432 | 170.9 | 0.042725 | 0.042963 | 171.85 | 0.0432 | 0.011056 | 30486.9 | 30487.5 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 13:00:00.000 | 154.7 | 0.038675 | 152.7 | 0.038175 | 0.038425 | 153.7 | 0.038675 | 0.013012 | 30487.5 | 30488 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 13:15:00.000 | 179.7 | 0.044925 | 179.4 | 0.04485 | 0.044887 | 179.55 | 0.044925 | 0.0016708 | 30488 | 30488.6 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 13:30:00.000 | 204.8 | 0.0512 | 204.8 | 0.0512 | 0.0512 | 204.8 | 0.0512 | 0 | 30488.6 | 30489.2 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 13:45:00.000 | 233.5 | 0.058375 | 229.8 | 0.05745 | 0.057913 | 231.65 | 0.058375 | 0.015972 | 30489.2 | 30489.9 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 14:00:00.000 | 458 | 0.1145 | 450.7 | 0.11267 | 0.11359 | 454.35 | 0.1145 | 0.016067 | 30489.9 | 30491 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 14:15:00.000 | 415.2 | 0.1038 | 403 | 0.10075 | 0.10228 | 409.1 | 0.1038 | 0.029822 | 30491 | 30492.4 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 14:30:00.000 | 260.1 | 0.065025 | 235.7 | 0.058925 | 0.061975 | 247.9 | 0.065025 | 0.098427 | 30492.4 | 30493.4 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 14:45:00.000 | 341 | 0.08525 | 320.3 | 0.080075 | 0.082662 | 330.65 | 0.08525 | 0.062604 | 30493.4 | 30494.2 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 15:00:00.000 | 407.9 | 0.10197 | 373.1 | 0.093275 | 0.097625 | 390.5 | 0.10197 | 0.089117 | 30494.2 | 30495.4 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 15:15:00.000 | 243.1 | 0.060775 | 212 | 0.053 | 0.056887 | 227.55 | 0.060775 | 0.13667 | 30495.4 | 30496.3 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 15:30:00.000 | 221.5 | 0.055375 | 189.3 | 0.047325 | 0.05135 | 205.4 | 0.055375 | 0.15677 | 30496.3 | 30497 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 15:45:00.000 | 245.1 | 0.061275 | 205.4 | 0.05135 | 0.056313 | 225.25 | 0.061275 | 0.17625 | 30497 | 30497.7 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 16:00:00.000 | 240.9 | 0.060225 | 197 | 0.04925 | 0.054738 | 218.95 | 0.060225 | 0.2005 | 30497.7 | 30498.3 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 16:15:00.000 | 157.2 | 0.0393 | 108.9 | 0.027225 | 0.033263 | 133.05 | 0.0393 | 0.36302 | 30498.3 | 30498.9 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 16:30:00.000 | 92.3 | 0.023075 | 64.9 | 0.016225 | 0.01965 | 78.6 | 0.023075 | 0.3486 | 30498.9 | 30499.2 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 16:45:00.000 | 79 | 0.01975 | 69.5 | 0.017375 | 0.018563 | 74.25 | 0.01975 | 0.12795 | 30499.2 | 30499.4 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 17:00:00.000 | 75.8 | 0.01895 | 71.3 | 0.017825 | 0.018388 | 73.55 | 0.01895 | 0.061183 | 30499.4 | 30499.6 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 17:15:00.000 | 90.7 | 0.022675 | 79.5 | 0.019875 | 0.021275 | 85.1 | 0.022675 | 0.13161 | 30499.6 | 30499.9 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 17:30:00.000 | 92.6 | 0.02315 | 83.9 | 0.020975 | 0.022062 | 88.25 | 0.02315 | 0.098584 | 30499.9 | 30500.2 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 17:45:00.000 | 113.9 | 0.028475 | 109.7 | 0.027425 | 0.02795 | 111.8 | 0.028475 | 0.037567 | 30500.2 | 30500.5 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 18:00:00.000 | 135 | 0.03375 | 129.5 | 0.032375 | 0.033063 | 132.25 | 0.03375 | 0.041588 | 30500.5 | 30500.9 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 18:15:00.000 | 103.1 | 0.025775 | 98.5 | 0.024625 | 0.0252 | 100.8 | 0.025775 | 0.045635 | 30500.9 | 30501.3 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 18:30:00.000 | 146.5 | 0.036625 | 146.3 | 0.036575 | 0.0366 | 146.4 | 0.036625 | 0.0013661 | 30501.3 | 30501.6 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 18:45:00.000 | 101.4 | 0.02535 | 104.9 | 0.026225 | 0.025788 | 103.15 | 0.026225 | 0.033931 | 30501.6 | 30502 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 19:00:00.000 | 60.8 | 0.0152 | 61.4 | 0.01535 | 0.015275 | 61.1 | 0.01535 | 0.00982 | 30502 | 30502.3 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 19:15:00.000 | 59.5 | 0.014875 | 60.2 | 0.01505 | 0.014963 | 59.85 | 0.01505 | 0.011696 | 30502.3 | 30502.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 19:30:00.000 | 21.6 | 0.0054 | 21 | 0.00525 | 0.005325 | 0 | 0.005325 | 0.028169 | 30502.4 | 30502.5 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 19:45:00.000 | 10.6 | 0.00265 | 10.7 | 0.002675 | 0.0026625 | 0 | 0.0026625 | 0.0093897 | 30502.5 | 30502.6 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 20:00:00.000 | 2.4 | 0.0006 | 2.4 | 0.0006 | 0.0006 | 0 | 0.0006 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 20:15:00.000 | -0.4 | -0.0001 | -0.5 | -0.000125 | -0.0001125 | 0 | -0.0001125 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 20:30:00.000 | -1.9 | -0.000475 | -1.5 | -0.000375 | -0.000425 | 0 | -0.000425 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 20:45:00.000 | -3 | -0.00075 | -3 | -0.00075 | -0.00075 | 0 | -0.00075 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 21:00:00.000 | -1.6 | -0.0004 | -1.5 | -0.000375 | -0.0003875 | 0 | -0.0003875 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 21:15:00.000 | -2.1 | -0.000525 | -1.9 | -0.000475 | -0.0005 | 0 | -0.0005 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 21:30:00.000 | -0.3 | -7.5e-05 | -0.4 | -0.0001 | -8.75e-05 | 0 | -8.75e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 21:45:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 22:00:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 22:15:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 22:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 22:45:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 23:00:00.000 | -2 | -0.0005 | -1.6 | -0.0004 | -0.00045 | 0 | -0.00045 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 23:15:00.000 | -3 | -0.00075 | -2.5 | -0.000625 | -0.0006875 | 0 | -0.0006875 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 23:30:00.000 | -2.3 | -0.000575 | -2.4 | -0.0006 | -0.0005875 | 0 | -0.0005875 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
2026-05-06 | 23:45:00.000 | -2.2 | -0.00055 | -2.2 | -0.00055 | -0.00055 | 0 | -0.00055 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672
PR for each inverter |  |  | 2.8345 |  | 2.7422 | 2.7884 |  | 2.8465 |  |  |  | 34800 |  | 1.0255 | 1.0113 | 1.0148 | 1.0117 | 1.0113 | 0.99781 | 1.0006 | 1.0081 | 0.99597 | 0.98562 | 0.98723 | 1.0149 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 1.0104 | 1.0052 | 0.99896 | 1.0112 | 1.0193 | 1.0079 | 1.0051 | 0.99559 | 0.98962 | 0.99403 | 0.99085 | 0.99951 |  |  |  | 0 | 1.0051 | 0.99951 | 0.99848 | 1.0026 | 0.99235 | 0.99059 | 1.0073 | 0.98136 | 0.98708 | 0.98439 | 1.0042 | 1.0103 | #DIV/0! | #DIV/0! | #DIV/0! | 0 |  | 1.0015 |  | #DIV/0! | #DIV/0! | 2.7561e-05
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-06 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 06:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 06:45:00.000 | 0.8 | 1 | 1.3 | 1 | 3.5 | 1.1 | 1 | 1.3 | 0.9 | 1 | 0.9 | 1.4 | 1.2667 | 3.5 | 0.8 | 1 | 0.9 | 2.8 | 1.1 | 3.3 | 1.3 | 1.2 | 4.1 | 1.1 | 1 | 0.8 | 3 | 1.8 | 4.1 | 0.8 | 4 | 1.2 | 1.5 | 0.9 | 1.2 | 0.9 | 1 | 1 | 1.1 | 0.9 | 1.2 | 0.9 | 1.3167 | 4 | 0.9
2026-05-06 | 07:00:00.000 | 10.4 | 10.2 | 10.6 | 10.4 | 10.5 | 10.4 | 10.4 | 11 | 10.9 | 10.9 | 10.8 | 10.5 | 10.5833 | 11 | 10.2 | 9.9 | 10.4 | 10.6 | 10.1 | 10.2 | 11.1 | 10.5 | 11.8 | 11 | 10.4 | 11 | 11.2 | 10.6833 | 11.8 | 9.9 | 11.4 | 10.3 | 11 | 10.9 | 11.1 | 11.1 | 11.1 | 10.8 | 10.9 | 11 | 11.2 | 9.9 | 10.8917 | 11.4 | 9.9
2026-05-06 | 07:15:00.000 | 32 | 31.7 | 32.3 | 32.4 | 31.5 | 31.9 | 31.7 | 33.4 | 33.2 | 33 | 33.3 | 32.7 | 32.425 | 33.4 | 31.5 | 30.5 | 31.3 | 31.4 | 31.1 | 30.9 | 33.7 | 32.5 | 33.5 | 33.8 | 32.1 | 33.9 | 34 | 32.3917 | 34 | 30.5 | 33.1 | 32.9 | 33.5 | 34 | 33.8 | 34.3 | 34.3 | 33.6 | 33.5 | 32.8 | 34.3 | 31.2 | 33.4417 | 34.3 | 31.2
2026-05-06 | 07:30:00.000 | 39.7 | 39.3 | 39.9 | 40 | 39.8 | 39.2 | 38 | 41.3 | 41 | 40.8 | 41 | 40.3 | 40.025 | 41.3 | 38 | 37.5 | 38.6 | 38.6 | 38 | 38 | 41.4 | 39.8 | 41 | 41.3 | 39.2 | 40.3 | 41.3 | 39.5833 | 41.4 | 37.5 | 41.6 | 40.5 | 41.4 | 41.9 | 41.7 | 42.1 | 42.3 | 41.3 | 41.2 | 40.7 | 42.3 | 38.9 | 41.325 | 42.3 | 38.9
2026-05-06 | 07:45:00.000 | 39.1 | 38.7 | 39.1 | 39.6 | 39.3 | 39 | 39.3 | 41.2 | 40.7 | 40.4 | 40.4 | 39.7 | 39.7083 | 41.2 | 38.7 | 37.4 | 39.1 | 38.8 | 37.6 | 37.5 | 41.1 | 39.4 | 40.6 | 40.5 | 38.6 | 39.9 | 40.6 | 39.2583 | 41.1 | 37.4 | 41 | 40.6 | 40.9 | 41 | 40.9 | 40.8 | 41.2 | 40.3 | 39.2 | 40.4 | 41.2 | 37.5 | 40.4167 | 41.2 | 37.5
2026-05-06 | 08:00:00.000 | 42.8 | 42.3 | 42.7 | 43.3 | 42.8 | 42.5 | 43 | 45.1 | 44.4 | 44 | 44 | 43.3 | 43.35 | 45.1 | 42.3 | 40.9 | 42.8 | 42.4 | 40.9 | 40.9 | 44.8 | 42.8 | 44.2 | 43.9 | 41.9 | 43.7 | 42.6 | 42.65 | 44.8 | 40.9 | 44.7 | 44.4 | 44.6 | 44.7 | 44.7 | 42.8 | 45.1 | 43.9 | 44.3 | 44.2 | 44.8 | 41 | 44.1 | 45.1 | 41
2026-05-06 | 08:15:00.000 | 45.3 | 44.7 | 45.2 | 46 | 45.6 | 45.3 | 46.1 | 48.2 | 47.5 | 47 | 47.1 | 46.4 | 46.2 | 48.2 | 44.7 | 42.3 | 46.1 | 45.6 | 43.8 | 43.9 | 48.1 | 46 | 47.5 | 47.1 | 45 | 46.9 | 47.5 | 45.8167 | 48.1 | 42.3 | 47.5 | 47.4 | 47.3 | 47.3 | 47.2 | 46.7 | 47.4 | 46.2 | 46.7 | 46.8 | 47.4 | 42.8 | 46.725 | 47.5 | 42.8
2026-05-06 | 08:30:00.000 | 48.7 | 48 | 48.5 | 49.4 | 48.8 | 48.6 | 49.5 | 51.8 | 50.9 | 50.3 | 50.3 | 49.6 | 49.5333 | 51.8 | 48 | 47.1 | 49.5 | 48.9 | 46.8 | 46.9 | 51.4 | 49.1 | 50.7 | 50.3 | 48 | 50 | 50.6 | 49.1083 | 51.4 | 46.8 | 50.6 | 50.6 | 50.5 | 50.5 | 50.4 | 49.9 | 50.8 | 49.5 | 50 | 50.1 | 50.6 | 46.1 | 49.9667 | 50.8 | 46.1
2026-05-06 | 08:45:00.000 | 50.3 | 49.4 | 50 | 51 | 50.4 | 50.2 | 51.2 | 53.6 | 52.6 | 51.9 | 51.8 | 51.2 | 51.1333 | 53.6 | 49.4 | 48.8 | 51.3 | 50.6 | 48.4 | 48.5 | 53.1 | 50.6 | 52.3 | 51.8 | 49.5 | 51.5 | 50.2 | 50.55 | 53.1 | 48.4 | 52 | 52.2 | 51.9 | 51.8 | 51.7 | 51.1 | 52.1 | 50.7 | 51.3 | 51.5 | 51.9 | 47.4 | 51.3 | 52.2 | 47.4
2026-05-06 | 09:00:00.000 | 75.3 | 73.8 | 74 | 75.9 | 74.1 | 75.3 | 76.6 | 79.6 | 79.1 | 76.4 | 76.8 | 75.6 | 76.0417 | 79.6 | 73.8 | 74.5 | 77.3 | 76.1 | 72.7 | 74 | 79.5 | 74.8 | 77.1 | 75.7 | 72.3 | 76.2 | 76.7 | 75.575 | 79.5 | 72.3 | 75.1 | 76.4 | 75 | 75 | 75.3 | 73.9 | 76.1 | 73.3 | 73.5 | 73.9 | 76.3 | 68.6 | 74.3667 | 76.4 | 68.6
2026-05-06 | 09:15:00.000 | 66.8 | 65.1 | 65.6 | 67.4 | 66.3 | 65.9 | 67.6 | 71.5 | 69.6 | 68.5 | 68.4 | 67.7 | 67.5333 | 71.5 | 65.1 | 65.6 | 67.8 | 67 | 63.5 | 63.7 | 70.9 | 67.2 | 69.4 | 68.5 | 65.1 | 67 | 68.1 | 66.9833 | 70.9 | 63.5 | 70.1 | 70.6 | 70.1 | 70.3 | 70.3 | 69.2 | 70.7 | 65.7 | 68.6 | 69 | 69.8 | 64.2 | 69.05 | 70.7 | 64.2
2026-05-06 | 09:30:00.000 | 62.2 | 60.5 | 61.2 | 62.7 | 62 | 61.5 | 63 | 66.9 | 65 | 64.1 | 64 | 63.2 | 63.025 | 66.9 | 60.5 | 60.8 | 63.2 | 62.4 | 59.2 | 59.5 | 66.3 | 62.6 | 64.9 | 63.9 | 60.8 | 62.7 | 63.8 | 62.5083 | 66.3 | 59.2 | 65.5 | 65.8 | 65.8 | 65.8 | 65.3 | 64.7 | 65.8 | 63.8 | 64.4 | 64.8 | 65.1 | 60 | 64.7333 | 65.8 | 60
2026-05-06 | 09:45:00.000 | 92.5 | 90.6 | 92.1 | 93.7 | 93.5 | 94.1 | 96 | 100.4 | 98.8 | 96 | 97 | 95.1 | 94.9833 | 100.4 | 90.6 | 90.8 | 94.8 | 93.5 | 85.4 | 90.1 | 99.5 | 95.2 | 97.5 | 96.7 | 92.8 | 97.5 | 98.8 | 94.3833 | 99.5 | 85.4 | 99.4 | 98.9 | 97.7 | 98.2 | 88.3 | 92.3 | 99.5 | 95.8 | 96.7 | 96.4 | 99.2 | 88.5 | 95.9083 | 99.5 | 88.3
2026-05-06 | 10:00:00.000 | 132.7 | 130.5 | 129.2 | 135.1 | 132.1 | 129.2 | 130.8 | 139.5 | 137.5 | 135.6 | 135.4 | 135 | 133.55 | 139.5 | 129.2 | 128.6 | 133.4 | 133.7 | 125.3 | 127 | 138.7 | 133.2 | 138.1 | 139.1 | 133.6 | 135.3 | 141 | 133.9167 | 141 | 125.3 | 140.4 | 140.3 | 137.2 | 142 | 139.3 | 135 | 138.1 | 133.7 | 128.7 | 136.5 | 138.6 | 124.7 | 136.2083 | 142 | 124.7
2026-05-06 | 10:15:00.000 | 126.1 | 116.2 | 130.1 | 122.3 | 135.1 | 135.4 | 131.5 | 136.7 | 130.6 | 134.5 | 132.6 | 128.4 | 129.9583 | 136.7 | 116.2 | 126.3 | 136.7 | 128.1 | 129.5 | 128 | 134.1 | 130.4 | 130.4 | 124.8 | 120.4 | 131.7 | 134.4 | 129.5667 | 136.7 | 120.4 | 131.6 | 129.5 | 131.1 | 131.6 | 128.2 | 130.3 | 133 | 122.3 | 129.3 | 129.6 | 130.8 | 123.8 | 129.2583 | 133 | 122.3
2026-05-06 | 10:30:00.000 | 126.6 | 124.8 | 129.4 | 129.5 | 131.5 | 132.3 | 130.3 | 137 | 130.4 | 132.1 | 131.6 | 122 | 129.7917 | 137 | 122 | 121.9 | 130.9 | 130.6 | 124 | 125 | 135.1 | 128.9 | 133 | 128.2 | 126.8 | 131 | 133 | 129.0333 | 135.1 | 121.9 | 135.2 | 134.7 | 133.6 | 128.8 | 132.5 | 132.2 | 133.4 | 130.6 | 131.5 | 131.4 | 133.6 | 123.3 | 131.7333 | 135.2 | 123.3
2026-05-06 | 10:45:00.000 | 197 | 196.8 | 202.1 | 200.1 | 203.6 | 186.9 | 188.6 | 201.2 | 200.1 | 197.7 | 207.3 | 204.3 | 198.8083 | 207.3 | 186.9 | 198.1 | 195.4 | 204.3 | 199.3 | 199.4 | 207.6 | 203.4 | 203.9 | 206.9 | 202.4 | 206.7 | 205.9 | 202.775 | 207.6 | 195.4 | 194.1 | 210.1 | 205.4 | 208.4 | 204.8 | 207.7 | 198 | 199.9 | 204.6 | 196.3 | 193.6 | 193.3 | 201.35 | 210.1 | 193.3
2026-05-06 | 11:00:00.000 | 222.2 | 218.8 | 220.3 | 222.9 | 217.9 | 205.3 | 208.6 | 229.5 | 222.4 | 225.7 | 224.7 | 222.1 | 220.0333 | 229.5 | 205.3 | 209.2 | 219.9 | 217.7 | 209.5 | 210.4 | 227.6 | 217.3 | 224.1 | 222.8 | 214.4 | 213.3 | 223.8 | 217.5 | 227.6 | 209.2 | 224.2 | 229.4 | 230.2 | 230.4 | 219.6 | 212 | 230.3 | 227 | 229.4 | 229.4 | 228.4 | 215 | 225.4417 | 230.4 | 212
2026-05-06 | 11:15:00.000 | 109.9 | 108.1 | 109.1 | 111.6 | 112.6 | 111.3 | 114.3 | 117.2 | 115.1 | 113.9 | 113.6 | 112.1 | 112.4 | 117.2 | 108.1 | 106.3 | 111.9 | 110.4 | 105.8 | 106.4 | 116.1 | 110.8 | 115 | 113.8 | 109.1 | 113.2 | 114.8 | 111.1333 | 116.1 | 105.8 | 115.7 | 115.6 | 115 | 114.9 | 114.5 | 113.2 | 115.4 | 112.4 | 113.6 | 114 | 115.2 | 105.2 | 113.725 | 115.7 | 105.2
2026-05-06 | 11:30:00.000 | 134.6 | 133.2 | 133.3 | 136.8 | 140.1 | 136.9 | 137.9 | 143.9 | 143.9 | 139.7 | 140.9 | 138.5 | 138.3083 | 143.9 | 133.2 | 131.1 | 137.8 | 137.5 | 131.2 | 132.7 | 144.3 | 136.4 | 144.5 | 142.7 | 136.4 | 141.7 | 134 | 137.525 | 144.5 | 131.1 | 145.4 | 144.6 | 141.2 | 142.8 | 142.7 | 135.3 | 141.6 | 137.2 | 138.7 | 138.8 | 143.3 | 127.4 | 139.9167 | 145.4 | 127.4
2026-05-06 | 11:45:00.000 | 175.5 | 172.5 | 172.5 | 174.4 | 170.1 | 172.4 | 167.2 | 175.5 | 182.1 | 178.4 | 178 | 175.8 | 174.5333 | 182.1 | 167.2 | 164.2 | 172.8 | 169.9 | 164.1 | 165.1 | 181.9 | 172.7 | 179.5 | 178.1 | 170.8 | 177.7 | 179.6 | 173.0333 | 181.9 | 164.1 | 179.4 | 179.5 | 185.3 | 185.3 | 185.4 | 184.8 | 186.4 | 182.2 | 182.6 | 182.7 | 184.8 | 170.3 | 182.3917 | 186.4 | 170.3
2026-05-06 | 12:00:00.000 | 129.2 | 127.4 | 128.6 | 130.4 | 130 | 130.5 | 131.1 | 137.5 | 135.2 | 134.1 | 133.6 | 131.8 | 131.6167 | 137.5 | 127.4 | 124.2 | 130.9 | 128.8 | 124.3 | 125.2 | 136.8 | 130.5 | 135 | 134 | 128.8 | 134.7 | 130.3 | 130.2917 | 136.8 | 124.2 | 137.1 | 137.3 | 136.3 | 136.8 | 136 | 135.1 | 136.4 | 133.1 | 128.3 | 134.8 | 136.6 | 124.1 | 134.325 | 137.3 | 124.1
2026-05-06 | 12:15:00.000 | 95.4 | 94.2 | 94.8 | 96.3 | 95.5 | 96.2 | 96.7 | 101 | 99.4 | 98.3 | 98.1 | 96.5 | 96.8667 | 101 | 94.2 | 91.6 | 96.4 | 95.3 | 91.8 | 92.3 | 99.9 | 92.1 | 98.8 | 98.2 | 94.3 | 98.4 | 99.2 | 95.6917 | 99.9 | 91.6 | 100.3 | 99.8 | 99.5 | 99.5 | 99.1 | 98.2 | 99.7 | 97.5 | 98.5 | 95.3 | 99.9 | 90.9 | 98.1833 | 100.3 | 90.9
2026-05-06 | 12:30:00.000 | 71.7 | 70.8 | 71.3 | 72.2 | 71.2 | 71.7 | 72.2 | 75.6 | 74.4 | 73.6 | 71.4 | 72.3 | 72.3667 | 75.6 | 70.8 | 68.4 | 71.9 | 71.1 | 68.6 | 68.9 | 74.8 | 71.4 | 73.9 | 73.5 | 70.5 | 73.6 | 74.1 | 71.725 | 74.8 | 68.4 | 75.1 | 74.5 | 74.5 | 74.7 | 74.4 | 74 | 75.1 | 73.4 | 74 | 74 | 75 | 68.6 | 73.9417 | 75.1 | 68.6
2026-05-06 | 12:45:00.000 | 62.4 | 61.6 | 62.1 | 61.8 | 62.4 | 62.3 | 62.6 | 65.7 | 64.8 | 64.1 | 64.1 | 62.9 | 63.0667 | 65.7 | 61.6 | 59.3 | 62.2 | 61.5 | 59.5 | 59.7 | 65.1 | 62.1 | 64.3 | 64.1 | 61.4 | 64.1 | 64.5 | 62.3167 | 65.1 | 59.3 | 65.5 | 64.8 | 65 | 65.2 | 62.6 | 64.9 | 65.7 | 64.2 | 64.6 | 64.5 | 65.5 | 59.9 | 64.3667 | 65.7 | 59.9
2026-05-06 | 13:00:00.000 | 55.7 | 55 | 55.5 | 55.2 | 55.9 | 55.7 | 56 | 58.7 | 57.9 | 57.3 | 57.3 | 56.2 | 56.3667 | 58.7 | 55 | 53.2 | 55.8 | 55.2 | 53.4 | 53.6 | 58.3 | 55.6 | 57.6 | 57.4 | 55 | 57.6 | 57.9 | 55.8833 | 58.3 | 53.2 | 58.5 | 57.8 | 58 | 58.1 | 58 | 55.8 | 58.5 | 57.2 | 57.6 | 57.5 | 58.5 | 53.3 | 57.4 | 58.5 | 53.3
2026-05-06 | 13:15:00.000 | 64.4 | 63.6 | 64.2 | 64.3 | 64.9 | 64.5 | 64.7 | 68.1 | 67.3 | 66.6 | 66.5 | 65.3 | 65.3667 | 68.1 | 63.6 | 61.6 | 64.6 | 63.8 | 61.8 | 62 | 67.9 | 64.8 | 67.2 | 67 | 64.2 | 67.2 | 67.5 | 64.9667 | 67.9 | 61.6 | 67.9 | 67.3 | 67.4 | 67.7 | 67.4 | 67.3 | 68 | 64.1 | 67 | 66.9 | 67.9 | 61.8 | 66.725 | 68 | 61.8
2026-05-06 | 13:30:00.000 | 73.1 | 72.3 | 73 | 73.3 | 73.9 | 73.5 | 74 | 77.5 | 76.8 | 76.1 | 76.1 | 74.7 | 74.525 | 77.5 | 72.3 | 70.6 | 74 | 73.2 | 70.8 | 71.1 | 74.9 | 74.2 | 77 | 76.9 | 73.7 | 77.2 | 77.6 | 74.2667 | 77.6 | 70.6 | 77.6 | 74.2 | 76.8 | 77 | 76.7 | 76.4 | 77.1 | 75.5 | 76.1 | 76.2 | 77.3 | 69.7 | 75.8833 | 77.6 | 69.7
2026-05-06 | 13:45:00.000 | 82 | 81.1 | 81.3 | 82.3 | 82.8 | 82.3 | 82.9 | 86.7 | 85.7 | 84.9 | 84.7 | 83.1 | 83.3167 | 86.7 | 81.1 | 79 | 82.7 | 81.9 | 79.4 | 79.8 | 86.3 | 82.3 | 85.4 | 85.3 | 79.4 | 85.7 | 86.2 | 82.7833 | 86.3 | 79 | 86.9 | 85.8 | 85.8 | 85.9 | 85.4 | 85.1 | 86.2 | 84.3 | 84.9 | 84.9 | 86.3 | 78.1 | 84.9667 | 86.9 | 78.1
2026-05-06 | 14:00:00.000 | 154.5 | 153.1 | 152.9 | 156.2 | 155.4 | 154.2 | 155.2 | 162.9 | 161.2 | 159.9 | 159.4 | 156.5 | 156.7833 | 162.9 | 152.9 | 148 | 154.7 | 153.3 | 148.7 | 149.5 | 162.8 | 155 | 155.8 | 161.1 | 154.2 | 161.2 | 161.8 | 155.5083 | 162.8 | 148 | 164.8 | 163.1 | 162.2 | 163 | 162.2 | 161.9 | 163.4 | 159.6 | 160.5 | 160.5 | 163.1 | 147.8 | 161.0083 | 164.8 | 147.8
2026-05-06 | 14:15:00.000 | 141.5 | 140.3 | 141.8 | 143.2 | 140.8 | 139.6 | 140.1 | 143.7 | 146.3 | 143.7 | 144 | 140.8 | 142.15 | 146.3 | 139.6 | 133.7 | 139 | 137.4 | 134.3 | 134.5 | 147 | 138.6 | 144 | 143.4 | 137.4 | 144.8 | 144.7 | 139.9 | 147 | 133.7 | 148.2 | 146.3 | 142.1 | 147.8 | 146.6 | 147.5 | 148.6 | 145.6 | 146 | 145.2 | 147.6 | 136.8 | 145.6917 | 148.6 | 136.8
2026-05-06 | 14:30:00.000 | 86 | 88 | 90.7 | 87.2 | 86.8 | 85.4 | 85.4 | 89.8 | 88.8 | 87.8 | 87.7 | 86.1 | 87.475 | 90.7 | 85.4 | 81.5 | 84.6 | 83.9 | 81.9 | 82.2 | 89.2 | 81.9 | 88.1 | 88 | 84.3 | 88.6 | 88.8 | 85.25 | 89.2 | 81.5 | 90.1 | 88.7 | 89.1 | 89.5 | 89.1 | 89.7 | 90.7 | 88.6 | 88.6 | 88 | 90.2 | 82.9 | 88.7667 | 90.7 | 82.9
2026-05-06 | 14:45:00.000 | 115 | 117.2 | 115.8 | 115.1 | 114.8 | 113.8 | 114 | 119.8 | 118.7 | 112.8 | 117.2 | 115.2 | 115.7833 | 119.8 | 112.8 | 108.9 | 108.8 | 112.3 | 109.5 | 110.4 | 119.4 | 113.7 | 118.1 | 118.1 | 113.3 | 119.1 | 119.6 | 114.2667 | 119.6 | 108.8 | 120.6 | 118.8 | 118.9 | 119.3 | 118.6 | 119.3 | 120.5 | 117.6 | 117.8 | 117.2 | 120.2 | 109.6 | 118.2 | 120.6 | 109.6
2026-05-06 | 15:00:00.000 | 140.9 | 138.6 | 136.3 | 132.2 | 131.3 | 129.9 | 130.1 | 137.4 | 135.9 | 134.4 | 134.3 | 131.9 | 134.4333 | 140.9 | 129.9 | 124 | 128.6 | 127.6 | 124.5 | 125.2 | 136.6 | 129.9 | 135 | 134.7 | 129.1 | 135.9 | 136.5 | 130.6333 | 136.6 | 124 | 137.9 | 136.3 | 136.8 | 137.6 | 137.4 | 138.7 | 140.1 | 136.3 | 136.2 | 130.6 | 138.4 | 127.3 | 136.1333 | 140.1 | 127.3
2026-05-06 | 15:15:00.000 | 88.7 | 86.2 | 82.9 | 77.7 | 77.2 | 76.3 | 76.3 | 80.7 | 80 | 79.2 | 79.1 | 77.9 | 80.1833 | 88.7 | 76.3 | 73.1 | 75.5 | 74.9 | 73.3 | 73.9 | 80.7 | 76.9 | 79.8 | 79.8 | 76.5 | 80.6 | 81.1 | 77.175 | 81.1 | 73.1 | 81.5 | 80.1 | 80.6 | 81 | 77.8 | 81.7 | 82.4 | 80.2 | 80 | 79.4 | 81.8 | 75.2 | 80.1417 | 82.4 | 75.2
2026-05-06 | 15:30:00.000 | 79.6 | 77.8 | 74.6 | 70 | 69.7 | 69 | 69.1 | 72.8 | 72 | 71.2 | 71 | 70.2 | 72.25 | 79.6 | 69 | 66.1 | 68.3 | 67.8 | 66.5 | 67.4 | 72.4 | 68.8 | 71.5 | 71.5 | 68.7 | 70 | 72.9 | 69.325 | 72.9 | 66.1 | 73.6 | 72 | 72.2 | 72.4 | 72 | 72.8 | 73.6 | 71.8 | 71.7 | 71.1 | 73.6 | 67.2 | 72 | 73.6 | 67.2
2026-05-06 | 15:45:00.000 | 86.7 | 85.9 | 80.8 | 74.8 | 74.4 | 73.7 | 71.2 | 77.9 | 77.2 | 76.3 | 76.2 | 75.4 | 77.5417 | 86.7 | 71.2 | 70.7 | 73 | 72.4 | 71.1 | 72 | 77.8 | 73.9 | 76.8 | 76.8 | 73.7 | 77.9 | 78.4 | 74.5417 | 78.4 | 70.7 | 79 | 77.3 | 77.5 | 77.8 | 77.4 | 78.4 | 79.1 | 77 | 76.9 | 76.2 | 79 | 72.1 | 77.3083 | 79.1 | 72.1
2026-05-06 | 16:00:00.000 | 83.9 | 84.1 | 78.7 | 73.1 | 72.9 | 69.8 | 72.5 | 75.5 | 74.7 | 73.9 | 73.8 | 72.9 | 75.4833 | 84.1 | 69.8 | 69.1 | 71.5 | 70.9 | 69.6 | 70.4 | 75 | 71.3 | 74 | 73.9 | 70.9 | 74.9 | 75.3 | 72.2333 | 75.3 | 69.1 | 76 | 74.2 | 74.3 | 74.6 | 74.2 | 74.9 | 75.9 | 74 | 74 | 73.3 | 76.1 | 69.7 | 74.2667 | 76.1 | 69.7
2026-05-06 | 16:15:00.000 | 56.2 | 55.8 | 49.5 | 42.6 | 42.3 | 41.9 | 41.9 | 44.1 | 43.6 | 43.1 | 43 | 42.6 | 45.55 | 56.2 | 41.9 | 40 | 41.3 | 41 | 40.2 | 40.6 | 43.8 | 41.6 | 43.2 | 43.1 | 41.3 | 43.6 | 43.9 | 41.9667 | 43.9 | 40 | 44.6 | 43.5 | 43.8 | 43.9 | 43.8 | 44.3 | 44.9 | 43.7 | 43.5 | 43 | 44.7 | 41.2 | 43.7417 | 44.9 | 41.2
2026-05-06 | 16:30:00.000 | 33.9 | 33.6 | 29.9 | 25.9 | 25.7 | 25.5 | 25.5 | 26.9 | 26.6 | 26.3 | 26.2 | 25.2 | 27.6 | 33.9 | 25.2 | 24.3 | 25.1 | 24.9 | 24.4 | 24.8 | 26.8 | 25.5 | 26.4 | 26.4 | 25.3 | 26.7 | 27 | 25.6333 | 27 | 24.3 | 27.3 | 26.5 | 26.7 | 26.7 | 26.7 | 27 | 27.3 | 26.6 | 26.5 | 26.2 | 27.4 | 25.1 | 26.6667 | 27.4 | 25.1
2026-05-06 | 16:45:00.000 | 27.8 | 27.3 | 26.5 | 25.4 | 25.5 | 25.3 | 25.2 | 26.4 | 26.3 | 26 | 25.9 | 25.9 | 26.125 | 27.8 | 25.2 | 24.1 | 24.8 | 24.6 | 23.3 | 24.9 | 26.4 | 25.2 | 26.2 | 26.3 | 25.2 | 26.7 | 27 | 25.3917 | 27 | 23.3 | 27.1 | 26.1 | 26.2 | 26.3 | 25.5 | 26.5 | 25.6 | 26.1 | 26 | 25.8 | 27.1 | 24.5 | 26.0667 | 27.1 | 24.5
2026-05-06 | 17:00:00.000 | 27 | 26.5 | 26.8 | 26.9 | 25.9 | 26.5 | 26.5 | 28 | 27.7 | 27.4 | 27.3 | 27.4 | 26.9917 | 28 | 25.9 | 24.5 | 26.1 | 25.9 | 25.5 | 26 | 28 | 26.8 | 27.9 | 28 | 27 | 28.6 | 29 | 26.9417 | 29 | 24.5 | 28.7 | 27.7 | 27.9 | 27 | 27.8 | 28.2 | 28.4 | 26.9 | 27.6 | 27.3 | 28.6 | 26 | 27.675 | 28.7 | 26
2026-05-06 | 17:15:00.000 | 31.8 | 31.2 | 31.6 | 31.8 | 31.7 | 31.3 | 30.3 | 31.9 | 31.6 | 31.3 | 31.2 | 31.2 | 31.4083 | 31.9 | 30.3 | 31 | 32 | 31.7 | 31.3 | 31.8 | 34.5 | 33.3 | 34.9 | 35.1 | 34.3 | 36.7 | 37.1 | 33.6417 | 37.1 | 31 | 31.5 | 30.4 | 30.5 | 30.6 | 30.6 | 31.2 | 31.4 | 30.6 | 30.4 | 30 | 31.4 | 28.8 | 30.6167 | 31.5 | 28.8
2026-05-06 | 17:30:00.000 | 32.3 | 31.7 | 32.1 | 32.3 | 32.2 | 31.8 | 31.1 | 32.8 | 32.5 | 32.3 | 32.1 | 31.8 | 32.0833 | 32.8 | 31.1 | 30.8 | 31.9 | 31.7 | 31.1 | 31.5 | 34.2 | 32.8 | 34.2 | 34.4 | 33.3 | 35.3 | 35.6 | 33.0667 | 35.6 | 30.8 | 31.8 | 30.6 | 30.8 | 30.8 | 30.2 | 31.9 | 32.2 | 31.4 | 31.3 | 30.3 | 31.7 | 29.6 | 31.05 | 32.2 | 29.6
2026-05-06 | 17:45:00.000 | 39.6 | 39.1 | 39.5 | 39.8 | 39.8 | 39.4 | 39.1 | 41 | 40.7 | 40.4 | 40.3 | 39.7 | 39.8667 | 41 | 39.1 | 38 | 38.2 | 39.2 | 38.3 | 38.7 | 42 | 40.2 | 41.8 | 41.9 | 40.4 | 42.6 | 43 | 40.3583 | 43 | 38 | 40.9 | 39.7 | 39.8 | 39.8 | 39.8 | 40.2 | 40.6 | 39.7 | 39.8 | 39.2 | 40.7 | 36.9 | 39.7583 | 40.9 | 36.9
2026-05-06 | 18:00:00.000 | 47 | 46.4 | 46.8 | 47.2 | 47.1 | 46.6 | 46.4 | 48.7 | 48.2 | 47.8 | 47.7 | 46.8 | 47.225 | 48.7 | 46.4 | 44.9 | 46.8 | 46.4 | 45.2 | 45.5 | 49.3 | 47.1 | 48.9 | 49 | 47.1 | 49.6 | 49.8 | 47.4667 | 49.8 | 44.9 | 48.3 | 47.2 | 47.3 | 47.4 | 47.4 | 47.8 | 48.3 | 47.3 | 47.3 | 46.7 | 48.1 | 44.1 | 47.2667 | 48.3 | 44.1
2026-05-06 | 18:15:00.000 | 36.2 | 35.6 | 35.9 | 36.1 | 36 | 35.5 | 35.1 | 37.1 | 36.7 | 36.3 | 36.1 | 35.6 | 36.0167 | 37.1 | 35.1 | 34 | 35.3 | 35.1 | 34.3 | 34.5 | 37.5 | 35.8 | 37.1 | 37.3 | 35.9 | 37.7 | 37.9 | 36.0333 | 37.9 | 34 | 37 | 36 | 36.2 | 36.3 | 36.4 | 36.7 | 37.1 | 36.3 | 36.3 | 35.8 | 37 | 34.1 | 36.2667 | 37.1 | 34.1
2026-05-06 | 18:30:00.000 | 50.2 | 49.7 | 50.1 | 50.5 | 50.4 | 50.1 | 50.3 | 52.8 | 52.2 | 51.5 | 51.4 | 50.4 | 50.8 | 52.8 | 49.7 | 47.8 | 50 | 49.4 | 47.9 | 48.3 | 51.9 | 49.5 | 51.2 | 49.6 | 49.1 | 51.3 | 51.6 | 49.8 | 51.9 | 47.8 | 52.8 | 52 | 51.9 | 52 | 51.6 | 51.6 | 52.5 | 51.4 | 51.9 | 51.8 | 52.7 | 48.1 | 51.6917 | 52.8 | 48.1
2026-05-06 | 18:45:00.000 | 34.6 | 34.3 | 34.2 | 34.9 | 34.5 | 34.1 | 34.4 | 36.3 | 35.9 | 35.5 | 35.4 | 34.9 | 34.9167 | 36.3 | 34.1 | 32.6 | 34.3 | 33.6 | 32.5 | 32.7 | 35.8 | 34.1 | 35.1 | 33.9 | 33.4 | 33.1 | 35 | 33.8417 | 35.8 | 32.5 | 36.3 | 36.4 | 36.2 | 36.5 | 36.6 | 36.6 | 37.2 | 36.1 | 36.3 | 36.5 | 36.8 | 33.5 | 36.25 | 37.2 | 33.5
2026-05-06 | 19:00:00.000 | 19.4 | 19.2 | 19.4 | 19.8 | 19.6 | 19.8 | 19.6 | 20.6 | 20.5 | 20.4 | 20.3 | 19.8 | 19.8667 | 20.6 | 19.2 | 18.5 | 19.5 | 19.3 | 18.7 | 18.6 | 20.5 | 19.5 | 20.4 | 19.8 | 19.4 | 20.4 | 20.5 | 19.5917 | 20.5 | 18.5 | 20.9 | 20.1 | 20.6 | 20.4 | 20.6 | 20.3 | 20.5 | 20.2 | 20.5 | 20.5 | 20.8 | 18.5 | 20.325 | 20.9 | 18.5
2026-05-06 | 19:15:00.000 | 19.1 | 18.9 | 19.1 | 19.4 | 19.3 | 19.5 | 19.3 | 20.3 | 20.1 | 20 | 19.9 | 19.4 | 19.525 | 20.3 | 18.9 | 18.1 | 19.1 | 18.8 | 18.2 | 18.1 | 19.9 | 19 | 19.7 | 19.7 | 18.7 | 19.6 | 19.7 | 19.05 | 19.9 | 18.1 | 20.5 | 19.9 | 20.3 | 20.2 | 20.3 | 20 | 20.2 | 19.9 | 20.3 | 19.5 | 20.5 | 18.4 | 20 | 20.5 | 18.4
2026-05-06 | 19:30:00.000 | 6.8 | 6.7 | 6.8 | 6.9 | 6.8 | 6.9 | 6.7 | 7 | 7 | 7 | 6.9 | 6.8 | 6.8583 | 7 | 6.7 | 6.3 | 6.6 | 6.6 | 6.4 | 6.4 | 7.1 | 6.8 | 7 | 7 | 6.7 | 7.1 | 7.1 | 6.7583 | 7.1 | 6.3 | 7.1 | 6.8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.1 | 6.5 | 6.9583 | 7.1 | 6.5
2026-05-06 | 19:45:00.000 | 3.5 | 3.4 | 3.5 | 3.6 | 3.5 | 3.6 | 3.5 | 3.6 | 3.7 | 3.7 | 3.6 | 3.5 | 3.5583 | 3.7 | 3.4 | 3.2 | 3.4 | 3.4 | 3.3 | 3.3 | 3.6 | 3.5 | 3.6 | 3.7 | 3.4 | 3.6 | 3.7 | 3.475 | 3.7 | 3.2 | 3.7 | 3.5 | 3.7 | 3.6 | 3.7 | 3.6 | 3.6 | 3.6 | 3.7 | 3.7 | 3.8 | 3.3 | 3.625 | 3.8 | 3.3
2026-05-06 | 20:00:00.000 | 1 | 0.7 | 1.1 | 1.2 | 0.8 | 1.1 | 1.2 | 1.1 | 1.2 | 1.2 | 1.1 | 1.1 | 1.0667 | 1.2 | 0.7 | 1.1 | 1.1 | 0.8 | 1.1 | 1 | 1.2 | 1.1 | 0.8 | 1.2 | 1.1 | 1.1 | 0.9 | 1.0417 | 1.2 | 0.8 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1583 | 1.2 | 1.1
2026-05-06 | 20:15:00.000 | 0.1 | 0.1 | 0.2 | 0.2 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.4 | 0.21667 | 0.5 | 0.1 | 0.2 | 0.3 | 0.8 | 0.2 | 0.7 | 0.2 | 0.3 | 0.5 | 0.3 | 0.2 | 0.1 | 0.2 | 0.33333 | 0.8 | 0.1 | 0.8 | 0.5 | 0.4 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.5 | 0.2 | 0.35833 | 0.8 | 0.2
2026-05-06 | 20:30:00.000 | 0.1 | 0 | 0.1 | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.17273 | 0.8 | 0 | 0.1 | 0.1 | 0.7 | 0.1 | 0.5 | 0.1 | 0.1 | 0.9 | 0.1 | 0.1 | 0.1 | 0.6 | 0.29167 | 0.9 | 0.1 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.14167 | 0.6 | 0.1
2026-05-06 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0 | 0 | 0 | 0.3 | 0 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.6 | 0.375 | 0.6 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0
2026-05-06 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.15 | 0.2 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0
2026-05-06 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.15 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-06 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320