## PR_Calc
PR CALCULATION
07 MAGGIO 2026 | [67 empty] | 7 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 49
RAW PR | [64 empty] | 0.91016 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 91.0159
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 91.0479
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 91.0159
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-07 | 00:00:00.000 | -0.9 | -0.000225 | -0.7 | -0.000175 | -0.0002 | 0 | -0.0002 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9014.3
2026-05-07 | 00:15:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 00:30:00.000 | -0.8 | -0.0002 | 0 | 0 | -0.0001 | 0 | -0.0001 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 00:45:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 02:15:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 02:30:00.000 | -0.9 | -0.000225 | -0.7 | -0.000175 | -0.0002 | 0 | -0.0002 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 02:45:00.000 | -0.8 | -0.0002 | -1 | -0.00025 | -0.000225 | 0 | -0.000225 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 03:15:00.000 | -0.3 | -7.5e-05 | 0 | 0 | -3.75e-05 | 0 | -3.75e-05 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 03:30:00.000 | -1.1 | -0.000275 | -0.2 | -5e-05 | -0.0001625 | 0 | -0.0001625 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 03:45:00.000 | -0.9 | -0.000225 | -0.3 | -7.5e-05 | -0.00015 | 0 | -0.00015 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 04:00:00.000 | -2 | -0.0005 | -1.6 | -0.0004 | -0.00045 | 0 | -0.00045 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 04:15:00.000 | -1.2 | -0.0003 | -0.4 | -0.0001 | -0.0002 | 0 | -0.0002 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 04:30:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 04:45:00.000 | -1 | -0.00025 | -0.6 | -0.00015 | -0.0002 | 0 | -0.0002 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 05:00:00.000 | -1.9 | -0.000475 | -1.8 | -0.00045 | -0.0004625 | 0 | -0.0004625 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 05:15:00.000 | -2.7 | -0.000675 | -2.9 | -0.000725 | -0.0007 | 0 | -0.0007 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 05:30:00.000 | -2.6 | -0.00065 | -1.8 | -0.00045 | -0.00055 | 0 | -0.00055 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 05:45:00.000 | -2 | -0.0005 | -1.9 | -0.000475 | -0.0004875 | 0 | -0.0004875 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 06:00:00.000 | -0.8 | -0.0002 | -1 | -0.00025 | -0.000225 | 0 | -0.000225 | 0 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 06:15:00.000 | 1.5 | 0.000375 | 1.6 | 0.0004 | 0.0003875 | 0 | 0.0003875 | 0.064516 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 06:30:00.000 | 20.8 | 0.0052 | 21.2 | 0.0053 | 0.00525 | 0 | 0.00525 | 0.019048 | 30502.6 | 30502.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 06:45:00.000 | 47 | 0.01175 | 48.2 | 0.01205 | 0.0119 | 0 | 0.0119 | 0.02521 | 30502.6 | 30502.7 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 07:00:00.000 | 63.6 | 0.0159 | 63.8 | 0.01595 | 0.015925 | 63.7 | 0.01595 | 0.0031397 | 30502.7 | 30502.8 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 07:15:00.000 | 102.1 | 0.025525 | 101.6 | 0.0254 | 0.025462 | 101.85 | 0.025525 | 0.0049092 | 30502.8 | 30503 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 07:30:00.000 | 194.9 | 0.048725 | 194.1 | 0.048525 | 0.048625 | 194.5 | 0.048725 | 0.0041131 | 30503 | 30503.4 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 07:45:00.000 | 261.9 | 0.065475 | 263.1 | 0.065775 | 0.065625 | 262.5 | 0.065775 | 0.0045714 | 30503.4 | 30504.1 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 08:00:00.000 | 332 | 0.083 | 332.6 | 0.08315 | 0.083075 | 332.3 | 0.08315 | 0.0018056 | 30504.1 | 30504.9 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 08:15:00.000 | 416 | 0.104 | 416.5 | 0.10412 | 0.10406 | 416.25 | 0.10412 | 0.0012012 | 30504.9 | 30506 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 08:30:00.000 | 513.5 | 0.12837 | 515.7 | 0.12893 | 0.12865 | 514.6 | 0.12893 | 0.0042752 | 30506 | 30507.3 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 08:45:00.000 | 618.3 | 0.15457 | 619.5 | 0.15488 | 0.15473 | 618.9 | 0.15488 | 0.0019389 | 30507.3 | 30508.9 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 09:00:00.000 | 684.4 | 0.1711 | 684.3 | 0.17107 | 0.17109 | 684.35 | 0.1711 | 0.00014612 | 30508.9 | 30510.8 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 09:15:00.000 | 733.7 | 0.18343 | 732.8 | 0.1832 | 0.18331 | 733.25 | 0.18343 | 0.0012274 | 30510.8 | 30512.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 09:30:00.000 | 617.2 | 0.1543 | 618.1 | 0.15452 | 0.15441 | 617.65 | 0.15452 | 0.0014571 | 30512.9 | 30514.9 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 09:45:00.000 | 784.6 | 0.19615 | 779.3 | 0.19482 | 0.19549 | 781.95 | 0.19615 | 0.0067779 | 30514.9 | 30516.9 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 10:00:00.000 | 809.3 | 0.20232 | 801.7 | 0.20043 | 0.20137 | 805.5 | 0.20232 | 0.0094351 | 30516.9 | 30519.1 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 10:15:00.000 | 789.9 | 0.19747 | 782.5 | 0.19562 | 0.19655 | 786.2 | 0.19747 | 0.0094124 | 30519.1 | 30521.4 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 10:30:00.000 | 836.4 | 0.2091 | 824.5 | 0.20613 | 0.20761 | 830.45 | 0.2091 | 0.01433 | 30521.4 | 30523.7 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 10:45:00.000 | 800.1 | 0.20003 | 787.5 | 0.19687 | 0.19845 | 793.8 | 0.20003 | 0.015873 | 30523.7 | 30526 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 11:00:00.000 | 847.8 | 0.21195 | 833.5 | 0.20838 | 0.21016 | 840.65 | 0.21195 | 0.017011 | 30526 | 30528.3 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 11:15:00.000 | 739.1 | 0.18477 | 725 | 0.18125 | 0.18301 | 732.05 | 0.18477 | 0.019261 | 30528.3 | 30530.5 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 11:30:00.000 | 796.5 | 0.19912 | 778.8 | 0.1947 | 0.19691 | 787.65 | 0.19912 | 0.022472 | 30530.5 | 30532.6 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 11:45:00.000 | 932.7 | 0.23318 | 913.4 | 0.22835 | 0.23076 | 923.05 | 0.23318 | 0.020909 | 30532.6 | 30535 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 12:00:00.000 | 913.1 | 0.22828 | 894.6 | 0.22365 | 0.22596 | 903.85 | 0.22828 | 0.020468 | 30535 | 30537.4 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 12:15:00.000 | 768 | 0.192 | 751.5 | 0.18787 | 0.18994 | 759.75 | 0.192 | 0.021718 | 30537.4 | 30539.7 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 12:30:00.000 | 939.8 | 0.23495 | 918.5 | 0.22962 | 0.23229 | 929.15 | 0.23495 | 0.022924 | 30539.7 | 30541.9 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 12:45:00.000 | 770.2 | 0.19255 | 758.1 | 0.18952 | 0.19104 | 764.15 | 0.19255 | 0.015835 | 30541.9 | 30544.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 13:00:00.000 | 752.7 | 0.18818 | 739.7 | 0.18493 | 0.18655 | 746.2 | 0.18818 | 0.017422 | 30544.2 | 30546.2 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 13:15:00.000 | 899.7 | 0.22493 | 879.5 | 0.21987 | 0.2224 | 889.6 | 0.22493 | 0.022707 | 30546.2 | 30548.5 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 13:30:00.000 | 908.8 | 0.2272 | 886.6 | 0.22165 | 0.22442 | 897.7 | 0.2272 | 0.02473 | 30548.5 | 30550.8 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 13:45:00.000 | 803 | 0.20075 | 782.9 | 0.19572 | 0.19824 | 792.95 | 0.20075 | 0.025348 | 30550.8 | 30553 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 14:00:00.000 | 670 | 0.1675 | 658.4 | 0.1646 | 0.16605 | 664.2 | 0.1675 | 0.017465 | 30553 | 30555 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 14:15:00.000 | 589.5 | 0.14738 | 578 | 0.1445 | 0.14594 | 583.75 | 0.14738 | 0.0197 | 30555 | 30556.9 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 14:30:00.000 | 594.9 | 0.14872 | 587.1 | 0.14678 | 0.14775 | 591 | 0.14872 | 0.013198 | 30556.9 | 30558.6 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 14:45:00.000 | 569.3 | 0.14232 | 551.4 | 0.13785 | 0.14009 | 560.35 | 0.14232 | 0.031944 | 30558.6 | 30560.3 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 15:00:00.000 | 709.5 | 0.17738 | 692.7 | 0.17318 | 0.17528 | 701.1 | 0.17738 | 0.023962 | 30560.3 | 30562 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 15:15:00.000 | 866.1 | 0.21652 | 773.9 | 0.19348 | 0.205 | 820 | 0.21652 | 0.11244 | 30562 | 30564.3 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 15:30:00.000 | 818.2 | 0.20455 | 692.5 | 0.17313 | 0.18884 | 755.35 | 0.20455 | 0.16641 | 30564.3 | 30566.5 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 15:45:00.000 | 897.9 | 0.22448 | 743.4 | 0.18585 | 0.20516 | 820.65 | 0.22448 | 0.18827 | 30566.5 | 30568.7 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 16:00:00.000 | 819.5 | 0.20488 | 631.5 | 0.15787 | 0.18138 | 725.5 | 0.20488 | 0.25913 | 30568.7 | 30571.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 16:15:00.000 | 826.2 | 0.20655 | 637.3 | 0.15932 | 0.18294 | 731.75 | 0.20655 | 0.25815 | 30571.1 | 30573.1 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 16:30:00.000 | 784.4 | 0.1961 | 563.6 | 0.1409 | 0.1685 | 674 | 0.1961 | 0.3276 | 30573.1 | 30575.3 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 16:45:00.000 | 636.9 | 0.15923 | 467.1 | 0.11678 | 0.138 | 552 | 0.15923 | 0.30761 | 30575.3 | 30577.1 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 17:00:00.000 | 342.4 | 0.0856 | 309.2 | 0.0773 | 0.08145 | 325.8 | 0.0856 | 0.1019 | 30577.1 | 30578.5 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 17:15:00.000 | 354.8 | 0.0887 | 335.5 | 0.083875 | 0.086288 | 345.15 | 0.0887 | 0.055918 | 30578.5 | 30579.4 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 17:30:00.000 | 312 | 0.078 | 308.2 | 0.07705 | 0.077525 | 310.1 | 0.078 | 0.012254 | 30579.4 | 30580.4 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 17:45:00.000 | 191.3 | 0.047825 | 184.3 | 0.046075 | 0.04695 | 187.8 | 0.047825 | 0.037274 | 30580.4 | 30581.1 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 18:00:00.000 | 132.5 | 0.033125 | 127.9 | 0.031975 | 0.03255 | 130.2 | 0.033125 | 0.03533 | 30581.1 | 30581.6 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 18:15:00.000 | 165 | 0.04125 | 165.4 | 0.04135 | 0.0413 | 165.2 | 0.04135 | 0.0024213 | 30581.6 | 30582 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 18:30:00.000 | 148.2 | 0.03705 | 150 | 0.0375 | 0.037275 | 149.1 | 0.0375 | 0.012072 | 30582 | 30582.5 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 18:45:00.000 | 93.5 | 0.023375 | 93 | 0.02325 | 0.023312 | 93.25 | 0.023375 | 0.0053619 | 30582.5 | 30582.9 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 19:00:00.000 | 68.9 | 0.017225 | 68.2 | 0.01705 | 0.017137 | 68.55 | 0.017225 | 0.010212 | 30582.9 | 30583.1 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 19:15:00.000 | 35 | 0.00875 | 34.7 | 0.008675 | 0.0087125 | 0 | 0.0087125 | 0.0086083 | 30583.1 | 30583.3 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 19:30:00.000 | 17.7 | 0.004425 | 17.6 | 0.0044 | 0.0044125 | 0 | 0.0044125 | 0.0056657 | 30583.3 | 30583.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 19:45:00.000 | 8.5 | 0.002125 | 8.5 | 0.002125 | 0.002125 | 0 | 0.002125 | 0 | 30583.3 | 30583.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 20:00:00.000 | 1.7 | 0.000425 | 1.8 | 0.00045 | 0.0004375 | 0 | 0.0004375 | 0.057143 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 20:15:00.000 | -0.3 | -7.5e-05 | 0 | 0 | -3.75e-05 | 0 | -3.75e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 20:30:00.000 | -1 | -0.00025 | -0.7 | -0.000175 | -0.0002125 | 0 | -0.0002125 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 20:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 21:00:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 21:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 21:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 22:00:00.000 | -1 | -0.00025 | -0.9 | -0.000225 | -0.0002375 | 0 | -0.0002375 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 22:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 22:30:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 22:45:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 23:00:00.000 | -0.3 | -7.5e-05 | 0 | 0 | -3.75e-05 | 0 | -3.75e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 23:15:00.000 | -1.1 | -0.000275 | -0.6 | -0.00015 | -0.0002125 | 0 | -0.0002125 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 23:30:00.000 | -1.4 | -0.00035 | -1 | -0.00025 | -0.0003 | 0 | -0.0003 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
2026-05-07 | 23:45:00.000 | -1 | -0.00025 | -0.3 | -7.5e-05 | -0.0001625 | 0 | -0.0001625 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0606
PR for each inverter |  |  | 7.3297 |  | 6.9526 | 7.1411 |  | 7.3337 |  |  |  | 80800 |  | 0.92144 | 0.91191 | 0.92011 | 0.92191 | 0.91991 | 0.91896 | 0.92245 | 0.90399 | 0.89727 | 0.89816 | 0.89846 | 0.92717 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.92866 | 0.91853 | 0.91009 | 0.92659 | 0.93929 | 0.91125 | 0.91352 | 0.89754 | 0.90379 | 0.91281 | 0.90331 | 0.90661 |  |  |  | 0 | 0.90984 | 0.90582 | 0.89783 | 0.8866 | 0.90549 | 0.90929 | 0.91332 | 0.89308 | 0.89946 | 0.89245 | 0.9001 | 0.93023 | #DIV/0! | #DIV/0! | #DIV/0! | 0 |  | 0.91048 |  | #DIV/0! | #DIV/0! | 9.7525e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-07 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 06:30:00.000 | 4.2 | 4.1 | 4.5 | 4.5 | 5.1 | 4.4 | 4.2 | 4.4 | 4.4 | 4.3 | 4.5 | 4.5 | 4.425 | 5.1 | 4.1 | 4.1 | 4.2 | 5 | 4.2 | 4.9 | 4.6 | 4.5 | 5.4 | 4.5 | 4.4 | 4.5 | 5.1 | 4.6167 | 5.4 | 4.1 | 5.3 | 4.4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.6 | 4.4 | 4.4 | 4.4 | 4.7 | 4.2 | 4.5333 | 5.3 | 4.2
2026-05-07 | 06:45:00.000 | 12.2 | 12 | 12.6 | 12.4 | 12.2 | 12.4 | 12.3 | 12.7 | 12.5 | 12.7 | 12.8 | 12.4 | 12.4333 | 12.8 | 12 | 11.6 | 11.9 | 12.7 | 11.9 | 11.7 | 12.7 | 12.7 | 12.8 | 13 | 12.5 | 13.2 | 13.8 | 12.5417 | 13.8 | 11.6 | 13.1 | 12.3 | 12.4 | 13 | 13 | 13.4 | 13.3 | 13 | 12.6 | 12.5 | 13.3 | 12 | 12.825 | 13.4 | 12
2026-05-07 | 07:00:00.000 | 17.6 | 17.4 | 17.9 | 18 | 17.9 | 17.7 | 17.4 | 18.1 | 18.2 | 18.2 | 18.3 | 18 | 17.8917 | 18.3 | 17.4 | 16.6 | 16.9 | 17.1 | 17.1 | 16.9 | 18.6 | 18.1 | 18.6 | 18.8 | 17.8 | 18.8 | 18.9 | 17.85 | 18.9 | 16.6 | 19 | 17.8 | 18.4 | 18.8 | 18.8 | 19.3 | 19.3 | 18.9 | 18.7 | 18 | 19.2 | 17.6 | 18.65 | 19.3 | 17.6
2026-05-07 | 07:15:00.000 | 30.1 | 29.8 | 30.6 | 30.5 | 30.5 | 30.2 | 29.8 | 31 | 31 | 30.9 | 31.2 | 30.6 | 30.5167 | 31.2 | 29.8 | 28.4 | 29.1 | 29.3 | 29.2 | 29 | 31.5 | 30.5 | 31.3 | 31.7 | 30.1 | 31.8 | 31.9 | 30.3167 | 31.9 | 28.4 | 31.8 | 30.3 | 31.1 | 31.6 | 31.5 | 32.1 | 32.3 | 31.5 | 31.3 | 30.5 | 32.3 | 29.4 | 31.3083 | 32.3 | 29.4
2026-05-07 | 07:30:00.000 | 57.8 | 57.3 | 58.6 | 58.6 | 58.4 | 57.7 | 57.1 | 59.5 | 59.3 | 59.2 | 59.8 | 58.6 | 58.4917 | 59.8 | 57.1 | 54.7 | 55.6 | 56.2 | 56 | 55.8 | 60.2 | 58.3 | 60.1 | 60.9 | 57.7 | 60.7 | 60.6 | 58.0667 | 60.9 | 54.7 | 61.2 | 58.6 | 60.2 | 61.3 | 61 | 62.2 | 61.9 | 60.7 | 60.1 | 58.7 | 62 | 56.6 | 60.375 | 62.2 | 56.6
2026-05-07 | 07:45:00.000 | 79.9 | 76.6 | 80.6 | 81 | 80.8 | 79.7 | 79.5 | 82.8 | 82.3 | 82 | 82.8 | 81 | 80.75 | 82.8 | 76.6 | 76 | 77.8 | 78.5 | 77.4 | 77.3 | 83.7 | 80.8 | 83.4 | 84 | 79.8 | 83.6 | 83.3 | 80.4667 | 84 | 76 | 84.3 | 81.6 | 83.5 | 84.9 | 84.5 | 85.5 | 85.4 | 83.6 | 83.1 | 81.7 | 85.6 | 77.8 | 83.4583 | 85.6 | 77.8
2026-05-07 | 08:00:00.000 | 103.1 | 102.1 | 103.9 | 104.7 | 104.5 | 103.4 | 103.5 | 107.6 | 106.4 | 106.1 | 107 | 104.7 | 104.75 | 107.6 | 102.1 | 99 | 101.8 | 102.3 | 100.4 | 100.4 | 108.4 | 104.5 | 107.6 | 107.9 | 102.7 | 107.4 | 107 | 104.1167 | 108.4 | 99 | 108.4 | 106 | 107.8 | 109.4 | 109.1 | 109.7 | 109.9 | 107.1 | 107 | 105.7 | 109.7 | 99.4 | 107.4333 | 109.9 | 99.4
2026-05-07 | 08:15:00.000 | 130.3 | 124.6 | 131.2 | 132.4 | 131.6 | 130.7 | 131.6 | 137.1 | 135.2 | 134 | 135.2 | 132.4 | 132.1917 | 137.1 | 124.6 | 125.4 | 129.3 | 129.8 | 126.4 | 126.6 | 137.4 | 131.9 | 136 | 136.1 | 129.6 | 134.9 | 134.4 | 131.4833 | 137.4 | 125.4 | 137.1 | 134.8 | 136.8 | 138.4 | 138.3 | 134.1 | 138.9 | 135.5 | 135.8 | 134.2 | 138 | 125.9 | 135.65 | 138.9 | 125.9
2026-05-07 | 08:30:00.000 | 161.5 | 160.1 | 162.3 | 163.9 | 163.1 | 162.3 | 163.8 | 170.3 | 167.3 | 166.3 | 167.4 | 163.9 | 164.35 | 170.3 | 160.1 | 156.1 | 161.4 | 161.5 | 156.7 | 157.1 | 170.9 | 163 | 168.5 | 168 | 160.1 | 166.5 | 166 | 162.9833 | 170.9 | 156.1 | 168.9 | 167.1 | 163.9 | 171.1 | 170.8 | 170.6 | 171.9 | 167 | 167.5 | 166.5 | 170.4 | 155.4 | 167.5917 | 171.9 | 155.4
2026-05-07 | 08:45:00.000 | 195.7 | 193.8 | 196 | 198.4 | 197.3 | 196.5 | 198.9 | 206.5 | 195.7 | 201.2 | 202.4 | 197.9 | 198.3583 | 206.5 | 193.8 | 188.8 | 196.1 | 195.7 | 189.3 | 189.9 | 206 | 196.5 | 196.2 | 202.2 | 192.9 | 200.2 | 199.5 | 196.1083 | 206 | 188.8 | 203.3 | 202.4 | 204 | 206.3 | 206.2 | 205.3 | 207.4 | 201.1 | 201.7 | 201.4 | 205 | 187.7 | 202.65 | 207.4 | 187.7
2026-05-07 | 09:00:00.000 | 217.8 | 215.2 | 217.9 | 220.6 | 219.2 | 219.1 | 222.5 | 231.7 | 219.1 | 224.7 | 225.6 | 221 | 221.2 | 231.7 | 215.2 | 211.5 | 220 | 218.7 | 210.3 | 211.2 | 230.1 | 219.1 | 227 | 225.1 | 215 | 222.8 | 222.2 | 219.4167 | 230.1 | 210.3 | 225.7 | 226.5 | 226.8 | 228.8 | 228.3 | 226.7 | 229.9 | 222.6 | 223.9 | 224.7 | 227.2 | 207.9 | 224.9167 | 229.9 | 207.9
2026-05-07 | 09:15:00.000 | 234.9 | 231.7 | 234.1 | 237.1 | 235.1 | 235.4 | 239.4 | 250.1 | 244.9 | 242.3 | 242.7 | 238 | 238.8083 | 250.1 | 231.7 | 227 | 236.7 | 234.8 | 225.9 | 227 | 239.6 | 235.6 | 244.6 | 242.5 | 231.7 | 240.8 | 243.3 | 235.7917 | 244.6 | 225.9 | 245.5 | 243.7 | 244.3 | 245.9 | 244.6 | 244.1 | 247.6 | 239.7 | 241.1 | 242.3 | 244.5 | 224.2 | 242.2917 | 247.6 | 224.2
2026-05-07 | 09:30:00.000 | 192 | 195.3 | 198.7 | 195.6 | 199.2 | 199.9 | 203.5 | 209.9 | 208.3 | 205.9 | 206.2 | 199.2 | 201.1417 | 209.9 | 192 | 192.3 | 199 | 198.1 | 191.1 | 190.9 | 209.5 | 200.1 | 208 | 206.3 | 197.5 | 204.2 | 207.4 | 200.3667 | 209.5 | 190.9 | 208.7 | 209.2 | 208 | 210 | 210.1 | 207.9 | 211.6 | 203.5 | 203.6 | 204.5 | 208.6 | 182 | 205.6417 | 211.6 | 182
2026-05-07 | 09:45:00.000 | 250 | 238.3 | 249.3 | 252.3 | 250.3 | 250.2 | 253.4 | 229.2 | 260.3 | 257.2 | 257.6 | 252.5 | 250.05 | 260.3 | 229.2 | 239.9 | 251.6 | 245.7 | 239.8 | 241.5 | 262.6 | 248.8 | 257.7 | 256.5 | 245.8 | 256.2 | 259.5 | 250.4667 | 262.6 | 239.8 | 262 | 260.5 | 259.6 | 261.1 | 259.9 | 259.2 | 263.8 | 254.6 | 256.7 | 257.1 | 260.3 | 239.1 | 257.825 | 263.8 | 239.1
2026-05-07 | 10:00:00.000 | 256.8 | 253.5 | 254.4 | 249.3 | 256.3 | 255.6 | 259.6 | 234.3 | 266.5 | 263.6 | 262.8 | 258.8 | 255.9583 | 266.5 | 234.3 | 244.9 | 255.8 | 247.9 | 244.7 | 245.8 | 268.1 | 254.6 | 255.4 | 263 | 252.2 | 262.4 | 266.1 | 255.075 | 268.1 | 244.7 | 259.3 | 267.2 | 256.5 | 263 | 267.2 | 265.9 | 270.4 | 252.8 | 263.3 | 263.5 | 267.4 | 244.7 | 261.7667 | 270.4 | 244.7
2026-05-07 | 10:15:00.000 | 249.7 | 237.9 | 248.1 | 250.6 | 249.6 | 249.4 | 252.7 | 239.7 | 258.8 | 247.4 | 256.3 | 251.8 | 249.3333 | 258.8 | 237.9 | 238.3 | 250.7 | 247.9 | 231.3 | 241.3 | 261 | 248 | 249.2 | 256 | 245.5 | 256 | 259.1 | 248.6917 | 261 | 231.3 | 262.2 | 261.3 | 259.4 | 256.7 | 260.3 | 258.4 | 263.2 | 245.2 | 255.9 | 256.7 | 260.8 | 237.6 | 256.475 | 263.2 | 237.6
2026-05-07 | 10:30:00.000 | 261.9 | 258.9 | 261.6 | 263.6 | 263 | 262.3 | 265.6 | 270.5 | 272.7 | 270.2 | 269.6 | 264.7 | 265.3833 | 272.7 | 258.9 | 250.3 | 262.6 | 260 | 251 | 252.9 | 273.6 | 260.5 | 269.9 | 269.1 | 257.4 | 269.1 | 272.2 | 262.3833 | 273.6 | 250.3 | 276.4 | 273.2 | 273.6 | 275.1 | 264.7 | 273 | 275.3 | 268.9 | 270.3 | 271.1 | 274.4 | 251.4 | 270.6167 | 276.4 | 251.4
2026-05-07 | 10:45:00.000 | 251.8 | 248.7 | 250 | 253.2 | 251.7 | 250.4 | 244.3 | 245.5 | 231.5 | 258.6 | 258 | 244.4 | 249.0083 | 258.6 | 231.5 | 238.7 | 251.3 | 248.4 | 240.2 | 241.7 | 261.7 | 241.3 | 258.5 | 257.6 | 247.2 | 257.8 | 260.4 | 250.4 | 261.7 | 238.7 | 263.5 | 262.3 | 261.4 | 262.4 | 261.5 | 259.7 | 264.3 | 256.7 | 248.4 | 250.7 | 262.6 | 239.5 | 257.75 | 264.3 | 239.5
2026-05-07 | 11:00:00.000 | 266.1 | 263.6 | 265.6 | 268.2 | 257.2 | 265.9 | 268.6 | 264.3 | 249.6 | 261.1 | 263.1 | 267.8 | 263.425 | 268.6 | 249.6 | 253.7 | 266.1 | 264 | 254.3 | 256.4 | 273.9 | 254.7 | 263.7 | 271.5 | 261.5 | 270.9 | 272.4 | 263.5917 | 273.9 | 253.7 | 275.8 | 273.8 | 265.4 | 275 | 274.1 | 273.7 | 255.8 | 270.5 | 263.4 | 273.1 | 273.9 | 247 | 268.4583 | 275.8 | 247
2026-05-07 | 11:15:00.000 | 228.1 | 226.5 | 230.7 | 230.6 | 226.8 | 229.1 | 223.1 | 232.2 | 224 | 232.2 | 235.3 | 230.3 | 229.075 | 235.3 | 223.1 | 211.9 | 229.2 | 214.8 | 205.1 | 222.7 | 234.2 | 227.7 | 233 | 236.6 | 228.2 | 229.1 | 237.2 | 225.8083 | 237.2 | 205.1 | 233.5 | 239.3 | 233.8 | 229.7 | 237.1 | 233.5 | 238.7 | 233 | 226.3 | 232 | 238.9 | 217.4 | 232.7667 | 239.3 | 217.4
2026-05-07 | 11:30:00.000 | 243.4 | 242.7 | 245.6 | 229.8 | 243.9 | 246.1 | 248.6 | 241.4 | 241.6 | 245.9 | 248.5 | 245.5 | 243.5833 | 248.6 | 229.8 | 235 | 245.8 | 241.8 | 234.5 | 241 | 250.7 | 235.6 | 245.7 | 246.8 | 241.4 | 247.9 | 239.9 | 242.175 | 250.7 | 234.5 | 242.5 | 247.5 | 242.9 | 238.6 | 246.2 | 249.4 | 246.8 | 236.6 | 249.2 | 249.9 | 247 | 222.5 | 243.2583 | 249.9 | 222.5
2026-05-07 | 11:45:00.000 | 280.1 | 279.8 | 279.3 | 280.6 | 279.9 | 279.7 | 280.5 | 281.4 | 279 | 280.5 | 280.6 | 280.1 | 280.125 | 281.4 | 279 | 273.4 | 279.6 | 278.9 | 273.7 | 276.1 | 281 | 269.8 | 280.7 | 280.6 | 277.1 | 280.9 | 281.2 | 277.75 | 281.2 | 269.8 | 281.1 | 280.8 | 280.8 | 281.3 | 280.5 | 271.1 | 280.9 | 280.7 | 281.1 | 280.9 | 280.7 | 275.9 | 279.65 | 281.3 | 271.1
2026-05-07 | 12:00:00.000 | 271.9 | 270.2 | 271.4 | 273 | 261.9 | 262.7 | 273.9 | 278.5 | 272.9 | 261.7 | 264.2 | 272.1 | 269.5333 | 278.5 | 261.7 | 265.1 | 271.3 | 271.4 | 264.3 | 265.6 | 276.6 | 268.6 | 274.9 | 273.6 | 268.6 | 274 | 275.2 | 270.7667 | 276.6 | 264.3 | 277.4 | 276.1 | 276.2 | 276.3 | 276.5 | 275.9 | 277.1 | 274.5 | 275 | 275.4 | 275.8 | 265.2 | 275.1167 | 277.4 | 265.2
2026-05-07 | 12:15:00.000 | 229.7 | 234 | 236.5 | 229.1 | 228.9 | 237.1 | 237 | 247.2 | 240.6 | 229.7 | 237.3 | 235.1 | 235.1833 | 247.2 | 228.9 | 227.5 | 237.2 | 234.7 | 227.7 | 230.2 | 244.5 | 233.2 | 240.8 | 240 | 225.6 | 240.1 | 242.5 | 235.3333 | 244.5 | 225.6 | 245.9 | 244.4 | 244.4 | 232.6 | 242.3 | 241.3 | 236 | 241 | 241.8 | 243.1 | 244 | 228.5 | 240.4417 | 245.9 | 228.5
2026-05-07 | 12:30:00.000 | 271.7 | 272 | 270.7 | 273 | 273.1 | 271 | 262.9 | 275.9 | 273.6 | 273.1 | 272.7 | 271.3 | 271.75 | 275.9 | 262.9 | 268.5 | 272.2 | 271.5 | 268.3 | 269 | 274.8 | 272 | 263.9 | 274 | 271.7 | 274.4 | 275.1 | 271.2833 | 275.1 | 263.9 | 274.9 | 273.6 | 275.1 | 274.5 | 274.4 | 274.9 | 274.3 | 273.9 | 274 | 274.4 | 274 | 256.9 | 272.9083 | 275.1 | 256.9
2026-05-07 | 12:45:00.000 | 230.8 | 236.3 | 233.6 | 231.5 | 235.2 | 233.8 | 239.5 | 243.6 | 241.5 | 239.4 | 238 | 239.3 | 236.875 | 243.6 | 230.8 | 229.8 | 236.6 | 236.6 | 225.8 | 227.6 | 243.2 | 223.8 | 241 | 240.8 | 232.7 | 237.5 | 240.3 | 234.6417 | 243.2 | 223.8 | 214.6 | 242.8 | 231.1 | 242.7 | 241.4 | 241.3 | 244.4 | 241 | 242.3 | 240.3 | 243.9 | 230.7 | 238.0417 | 244.4 | 214.6
2026-05-07 | 13:00:00.000 | 225.7 | 223.3 | 226.7 | 219 | 227 | 217.7 | 226 | 233.6 | 230.8 | 231.1 | 230.6 | 225.9 | 226.45 | 233.6 | 217.7 | 219.3 | 218.3 | 215.4 | 220.4 | 221.2 | 231.9 | 219.2 | 231.1 | 229.8 | 223.4 | 229.8 | 230.4 | 224.1833 | 231.9 | 215.4 | 234.3 | 231.4 | 228.6 | 233.8 | 233.4 | 233.3 | 232 | 228.3 | 230.7 | 226.3 | 230.1 | 218.2 | 230.0333 | 234.3 | 218.2
2026-05-07 | 13:15:00.000 | 266.2 | 264.2 | 265.1 | 266.4 | 265.4 | 264 | 263.4 | 270.2 | 266.8 | 268.1 | 267.4 | 265.5 | 266.0583 | 270.2 | 263.4 | 250.8 | 264.4 | 262.5 | 258.2 | 259 | 269.3 | 262.7 | 266.4 | 265.2 | 263.3 | 266.7 | 257.3 | 262.15 | 269.3 | 250.8 | 271.7 | 249.3 | 258.8 | 260.7 | 259.7 | 268.6 | 269.3 | 259.1 | 269.9 | 258.9 | 259.3 | 260.5 | 262.15 | 271.7 | 249.3
2026-05-07 | 13:30:00.000 | 266.4 | 266.4 | 265 | 266.5 | 266 | 265.7 | 266.5 | 271.4 | 268.8 | 269.2 | 268.4 | 266.2 | 267.2083 | 271.4 | 265 | 259.8 | 266.4 | 264.8 | 260.6 | 262.2 | 270.5 | 264.7 | 259.9 | 270 | 265.5 | 266.7 | 269.1 | 265.0167 | 270.5 | 259.8 | 272.2 | 269.1 | 271.2 | 271.1 | 269.5 | 270.3 | 269.1 | 267.4 | 269.9 | 270 | 268.3 | 260.4 | 269.0417 | 272.2 | 260.4
2026-05-07 | 13:45:00.000 | 243.5 | 241.9 | 238.6 | 234.7 | 238.8 | 237.6 | 242.9 | 247.4 | 246 | 243.9 | 242.5 | 242.5 | 241.6917 | 247.4 | 234.7 | 232.5 | 243.3 | 230.2 | 214.3 | 238 | 248.2 | 239.5 | 244.8 | 243.7 | 229.7 | 244.7 | 245.8 | 237.8917 | 248.2 | 214.3 | 240.1 | 245.2 | 247.6 | 224.3 | 243.9 | 245 | 246.3 | 246.1 | 246.4 | 228.9 | 240.3 | 234.4 | 240.7083 | 247.6 | 224.3
2026-05-07 | 14:00:00.000 | 213.5 | 211.9 | 214.7 | 214 | 213.1 | 213.4 | 213.8 | 223.3 | 220.5 | 218.6 | 211.5 | 213.6 | 215.1583 | 223.3 | 211.5 | 204.9 | 213.1 | 210.3 | 205.2 | 207.3 | 220.9 | 213.1 | 219.1 | 218.8 | 212 | 220.5 | 221.5 | 213.8917 | 221.5 | 204.9 | 224 | 221.7 | 220.7 | 222.2 | 221.6 | 221.2 | 222.8 | 209.9 | 218.6 | 218 | 221.9 | 206.2 | 219.0667 | 224 | 206.2
2026-05-07 | 14:15:00.000 | 190.3 | 180 | 190.4 | 191.9 | 191.8 | 189.7 | 190.9 | 202.2 | 191.3 | 198.9 | 198 | 193.3 | 192.3917 | 202.2 | 180 | 181.3 | 188.8 | 187.9 | 183.1 | 183.1 | 194 | 191 | 192.5 | 197.8 | 189.1 | 198.5 | 198.6 | 190.475 | 198.6 | 181.3 | 199.8 | 199.6 | 199.2 | 200.2 | 199.1 | 199.6 | 201.2 | 194.7 | 195.7 | 196.7 | 201.1 | 178.6 | 197.125 | 201.2 | 178.6
2026-05-07 | 14:30:00.000 | 185.5 | 192.5 | 192.6 | 193.3 | 194.1 | 191.3 | 192.3 | 202.1 | 200.4 | 202.2 | 200.5 | 194.7 | 195.125 | 202.2 | 185.5 | 182.8 | 191 | 187.2 | 183.5 | 186.2 | 203.7 | 194.6 | 199.7 | 198.9 | 185.6 | 201.3 | 200.7 | 192.9333 | 203.7 | 182.8 | 206.1 | 204 | 193.2 | 205.8 | 204.6 | 205.4 | 206.1 | 199.6 | 200.3 | 200.2 | 203.1 | 187.7 | 201.3417 | 206.1 | 187.7
2026-05-07 | 14:45:00.000 | 185.1 | 183.1 | 172.6 | 185.6 | 183.9 | 178.7 | 183 | 194.9 | 191.5 | 190.2 | 188.8 | 178 | 184.6167 | 194.9 | 172.6 | 174.4 | 182.3 | 180 | 175.2 | 176.7 | 191.1 | 180.3 | 188.3 | 188.9 | 181 | 189.2 | 181.1 | 182.375 | 191.1 | 174.4 | 184.4 | 188.4 | 191 | 182 | 187.4 | 190.3 | 192.7 | 180.1 | 189.4 | 188.9 | 184.2 | 177.2 | 186.3333 | 192.7 | 177.2
2026-05-07 | 15:00:00.000 | 220 | 218.2 | 218.5 | 220.8 | 217.7 | 218.2 | 219.6 | 225.8 | 223.9 | 222.7 | 222.8 | 215.9 | 220.3417 | 225.8 | 215.9 | 210.4 | 218.6 | 215.6 | 211.1 | 213.7 | 218.5 | 214.3 | 214.4 | 223.5 | 218.3 | 224.2 | 225.5 | 217.3417 | 225.5 | 210.4 | 227.3 | 218.2 | 224.2 | 224 | 222.8 | 223.8 | 225.1 | 223.4 | 217.7 | 223 | 224.7 | 211.9 | 222.175 | 227.3 | 211.9
2026-05-07 | 15:15:00.000 | 257.4 | 255.5 | 247.8 | 256.6 | 256.7 | 257 | 256.7 | 261.5 | 260.5 | 258.6 | 259.5 | 253 | 256.7333 | 261.5 | 247.8 | 249.9 | 256.6 | 255.1 | 250.7 | 252.2 | 259.8 | 256.4 | 259.3 | 259.2 | 255.5 | 259.2 | 259.8 | 256.1417 | 259.8 | 249.9 | 254.9 | 261.1 | 253.7 | 259.6 | 260.4 | 260.2 | 261.3 | 258.4 | 258.7 | 258.9 | 259.6 | 251.4 | 258.1833 | 261.3 | 251.4
2026-05-07 | 15:30:00.000 | 244.9 | 243.8 | 243.8 | 245.2 | 244.2 | 243.4 | 244.1 | 251.1 | 249.4 | 248.5 | 247.6 | 246.3 | 246.025 | 251.1 | 243.4 | 235.6 | 234.4 | 240.7 | 236.1 | 237.7 | 249 | 243.3 | 247.6 | 248.2 | 243.5 | 249.3 | 250.4 | 242.9833 | 250.4 | 234.4 | 251.2 | 247.8 | 247.3 | 235.7 | 248.3 | 250.5 | 250.2 | 236.7 | 248.4 | 245.1 | 240.8 | 239.7 | 245.1417 | 251.2 | 235.7
2026-05-07 | 15:45:00.000 | 263.3 | 261.4 | 263.6 | 262.8 | 263.9 | 263.2 | 262.7 | 268.8 | 267 | 267 | 267.2 | 264.2 | 264.5917 | 268.8 | 261.4 | 255.5 | 261.6 | 261.5 | 254.8 | 256.6 | 268.2 | 262.2 | 267.3 | 266.9 | 262.4 | 267.2 | 267.8 | 262.6667 | 268.2 | 254.8 | 269.4 | 267.8 | 256.4 | 248.3 | 259 | 268.3 | 269 | 258.9 | 267.3 | 263.3 | 259.5 | 258.8 | 262.1667 | 269.4 | 248.3
2026-05-07 | 16:00:00.000 | 243.8 | 242.3 | 242.1 | 242.9 | 242.8 | 241.1 | 242.3 | 246.2 | 245.3 | 245.5 | 244 | 242.7 | 243.4167 | 246.2 | 241.1 | 233.9 | 235.2 | 239.4 | 226.8 | 237.4 | 245 | 240.4 | 244.9 | 244.6 | 240.4 | 244 | 244.6 | 239.7167 | 245 | 226.8 | 246.2 | 246 | 241.4 | 215.6 | 245.7 | 245.6 | 239.8 | 245 | 245.3 | 238.5 | 233.6 | 239.8 | 240.2083 | 246.2 | 215.6
2026-05-07 | 16:15:00.000 | 245.4 | 243.3 | 243.4 | 244.7 | 236.3 | 242.7 | 244.8 | 254.2 | 251.3 | 250.3 | 249 | 246.8 | 246.0167 | 254.2 | 236.3 | 233.6 | 242.1 | 240.2 | 234.3 | 237.5 | 251.4 | 241.9 | 249.2 | 249.7 | 242.5 | 250.9 | 252.7 | 243.8333 | 252.7 | 233.6 | 253.7 | 250.9 | 243.7 | 215.5 | 247.6 | 251 | 244.1 | 249.2 | 239.1 | 238.4 | 233.7 | 236.7 | 241.9667 | 253.7 | 215.5
2026-05-07 | 16:30:00.000 | 232.7 | 234.6 | 236.3 | 234.4 | 228 | 234.7 | 227.5 | 248.9 | 237.1 | 244.5 | 244.3 | 238 | 236.75 | 248.9 | 227.5 | 223.9 | 233.7 | 230.9 | 224 | 222.9 | 246.5 | 232.9 | 238.2 | 243.2 | 233.5 | 244 | 246.3 | 235 | 246.5 | 222.9 | 248.3 | 247.3 | 234.8 | 195.9 | 242.7 | 247.8 | 249.8 | 244.2 | 244.2 | 224.6 | 218.1 | 222 | 234.975 | 249.8 | 195.9
2026-05-07 | 16:45:00.000 | 192 | 175.4 | 190 | 190.8 | 190.1 | 188.6 | 175.3 | 201.9 | 200.2 | 196.3 | 187.9 | 195.3 | 190.3167 | 201.9 | 175.3 | 180.4 | 188.2 | 185 | 181.4 | 185.5 | 200.1 | 181.4 | 196.6 | 197.6 | 190.1 | 199.1 | 201.7 | 190.5917 | 201.7 | 180.4 | 203.3 | 198.2 | 191.1 | 160.2 | 187.1 | 199.7 | 201.9 | 196.1 | 197.7 | 177.9 | 174.1 | 185.1 | 189.3667 | 203.3 | 160.2
2026-05-07 | 17:00:00.000 | 107.6 | 105.7 | 106.3 | 106.1 | 106.2 | 105.1 | 105.3 | 112.4 | 110.9 | 109.5 | 109 | 108.4 | 107.7083 | 112.4 | 105.1 | 100 | 103.4 | 102.5 | 100.4 | 102.8 | 110.4 | 105.4 | 106 | 110.2 | 106.6 | 112.3 | 113.4 | 106.1167 | 113.4 | 100 | 114 | 110.9 | 109.9 | 108 | 111 | 112.1 | 113.8 | 110.3 | 110.5 | 108.8 | 107.9 | 104.6 | 110.15 | 114 | 104.6
2026-05-07 | 17:15:00.000 | 110.5 | 108.7 | 109.1 | 109.2 | 109.7 | 108 | 107.4 | 113.8 | 112.4 | 111.3 | 110.7 | 110.2 | 110.0833 | 113.8 | 107.4 | 104.5 | 108.5 | 107.4 | 105.2 | 107.6 | 114.9 | 110 | 114.7 | 115.7 | 112.5 | 118.7 | 119.6 | 111.6083 | 119.6 | 104.5 | 113.5 | 110.2 | 109.9 | 110.6 | 109.6 | 111.3 | 113.3 | 110 | 110.2 | 109.6 | 113.2 | 104.5 | 110.4917 | 113.5 | 104.5
2026-05-07 | 17:30:00.000 | 100.4 | 99.1 | 99.1 | 99.3 | 99.3 | 98.2 | 98.2 | 105.1 | 103.7 | 102.5 | 101.7 | 100.4 | 100.5833 | 105.1 | 98.2 | 94 | 97.8 | 96.7 | 94 | 92.8 | 103.3 | 98.5 | 102.3 | 102.9 | 99 | 103.7 | 104.5 | 99.125 | 104.5 | 92.8 | 104.7 | 102 | 101.9 | 102.3 | 102.1 | 103.4 | 104.9 | 102 | 102.5 | 101.6 | 104.2 | 96.2 | 102.3167 | 104.9 | 96.2
2026-05-07 | 17:45:00.000 | 63.4 | 62.6 | 62.9 | 63.2 | 63 | 62.4 | 62 | 66 | 65.1 | 64.4 | 64.1 | 63.2 | 63.525 | 66 | 62 | 59.8 | 62.2 | 61.5 | 59.9 | 60.6 | 65.9 | 62.9 | 65.4 | 65.5 | 63 | 66.2 | 66.6 | 63.2917 | 66.6 | 59.8 | 65.1 | 63.6 | 63.8 | 64.1 | 64.1 | 64.8 | 65.7 | 63.9 | 64.1 | 63.4 | 65.2 | 60.2 | 64 | 65.7 | 60.2
2026-05-07 | 18:00:00.000 | 44.9 | 44.3 | 44.7 | 45 | 44.9 | 44.4 | 44.2 | 46.9 | 46.3 | 45.9 | 45.7 | 45.1 | 45.1917 | 46.9 | 44.2 | 42.7 | 44.5 | 44 | 43 | 43.3 | 47.2 | 45.1 | 46.9 | 47 | 45.3 | 47.5 | 47.9 | 45.3667 | 47.9 | 42.7 | 46.4 | 45.2 | 45.3 | 45.4 | 45.4 | 45.9 | 46.4 | 45.3 | 45.4 | 44.8 | 46.3 | 42.3 | 45.3417 | 46.4 | 42.3
2026-05-07 | 18:15:00.000 | 56 | 55.4 | 55.7 | 56.1 | 56 | 55.5 | 55.5 | 59 | 58.3 | 57.7 | 57.5 | 56.6 | 56.6083 | 59 | 55.4 | 53.2 | 55.5 | 54.9 | 53.3 | 53.8 | 58.5 | 55.9 | 58 | 58 | 55.8 | 58.3 | 58.8 | 56.1667 | 58.8 | 53.2 | 58.9 | 57.8 | 55.4 | 57.9 | 57.5 | 57.8 | 58.6 | 57.1 | 57.6 | 57.4 | 58.7 | 53.2 | 57.325 | 58.9 | 53.2
2026-05-07 | 18:30:00.000 | 50.4 | 49.9 | 50.2 | 50.7 | 50.5 | 50.1 | 50.3 | 53.3 | 52.7 | 52 | 51.9 | 51.1 | 51.0917 | 53.3 | 49.9 | 47.9 | 50.1 | 49.5 | 47.8 | 48.2 | 52.5 | 50.1 | 51.9 | 51.8 | 49.7 | 51.9 | 52.2 | 50.3 | 52.5 | 47.8 | 53 | 52.4 | 52.3 | 52.5 | 52.3 | 52.3 | 53.1 | 51.8 | 52.3 | 52.2 | 53.1 | 48.2 | 52.125 | 53.1 | 48.2
2026-05-07 | 18:45:00.000 | 31.5 | 31.2 | 31.4 | 31.7 | 31.5 | 31.4 | 31.4 | 33.1 | 32.7 | 32.4 | 32.4 | 31.8 | 31.875 | 33.1 | 31.2 | 29.9 | 31.3 | 30.9 | 30 | 30.1 | 32.9 | 31.5 | 32.5 | 32.5 | 31.1 | 32.6 | 32.8 | 31.5083 | 32.9 | 29.9 | 32.9 | 32.4 | 32.6 | 32.6 | 32.6 | 32.5 | 32.9 | 32.2 | 32.4 | 32.4 | 33 | 29.9 | 32.3667 | 33 | 29.9
2026-05-07 | 19:00:00.000 | 23.4 | 23.1 | 23.3 | 23.6 | 23.4 | 23.4 | 23.3 | 24.5 | 24.2 | 24 | 24 | 23.6 | 23.65 | 24.5 | 23.1 | 22.2 | 23.3 | 23 | 22.3 | 22.3 | 24.5 | 23.4 | 24.2 | 24.2 | 23.1 | 24.2 | 24.4 | 23.425 | 24.5 | 22.2 | 24.4 | 24 | 24.1 | 24.2 | 24.2 | 24.1 | 24.3 | 23.9 | 24 | 24 | 24.5 | 22.1 | 23.9833 | 24.5 | 22.1
2026-05-07 | 19:15:00.000 | 11.9 | 11.7 | 11.9 | 12 | 11.9 | 11.9 | 11.8 | 12.4 | 12.3 | 12.2 | 12.2 | 11.9 | 12.0083 | 12.4 | 11.7 | 11.2 | 11.8 | 11.6 | 11.3 | 11.3 | 12.4 | 11.9 | 12.3 | 12.3 | 11.7 | 12.3 | 12.4 | 11.875 | 12.4 | 11.2 | 12.4 | 12.1 | 12.2 | 12.2 | 12.3 | 12.2 | 12.3 | 12.1 | 12.2 | 12.1 | 12.4 | 11.2 | 12.1417 | 12.4 | 11.2
2026-05-07 | 19:30:00.000 | 6 | 5.9 | 6 | 6 | 6 | 6.1 | 5.9 | 6.2 | 6.2 | 6.2 | 6.1 | 6 | 6.05 | 6.2 | 5.9 | 5.6 | 5.9 | 5.8 | 5.6 | 5.6 | 6.2 | 6 | 6.2 | 6.2 | 5.9 | 6.2 | 6.3 | 5.9583 | 6.3 | 5.6 | 6.3 | 6 | 6.2 | 6.1 | 6.2 | 6.1 | 6.2 | 6.1 | 6.2 | 6.2 | 6.3 | 5.6 | 6.125 | 6.3 | 5.6
2026-05-07 | 19:45:00.000 | 2.7 | 2.7 | 2.7 | 2.8 | 2.7 | 2.9 | 2.8 | 2.9 | 2.9 | 2.9 | 2.9 | 2.8 | 2.8083 | 2.9 | 2.7 | 2.5 | 2.7 | 2.7 | 2.6 | 2.6 | 2.9 | 2.8 | 2.9 | 2.9 | 2.7 | 2.9 | 2.9 | 2.7583 | 2.9 | 2.5 | 3 | 2.7 | 2.9 | 2.8 | 2.9 | 2.8 | 2.8 | 2.9 | 2.9 | 2.9 | 3 | 2.6 | 2.85 | 3 | 2.6
2026-05-07 | 20:00:00.000 | 0.7 | 0.5 | 0.9 | 0.9 | 0.5 | 0.8 | 0.9 | 0.9 | 1 | 0.8 | 0.8 | 0.9 | 0.8 | 1 | 0.5 | 0.8 | 0.8 | 0.7 | 0.8 | 0.9 | 0.9 | 1 | 0.9 | 1 | 0.8 | 0.8 | 0.8 | 0.85 | 1 | 0.7 | 0.9 | 1 | 0.9 | 1 | 1 | 0.9 | 0.8 | 1 | 1 | 1 | 1 | 0.8 | 0.94167 | 1 | 0.8
2026-05-07 | 20:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.14167 | 0.4 | 0.1 | 0.1 | 0.2 | 0.8 | 0.1 | 0.8 | 0.1 | 0.2 | 1 | 0.2 | 0.1 | 0.1 | 0.8 | 0.375 | 1 | 0.1 | 0.8 | 0.4 | 0.3 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | 0.1 | 0.2 | 0.3 | 0.1 | 0.24167 | 0.8 | 0.1
2026-05-07 | 20:30:00.000 | 0 | 0 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.17 | 0.7 | 0 | 0.1 | 0.1 | 0.7 | 0.1 | 0.6 | 0.1 | 0.1 | 0.8 | 0.1 | 0.1 | 0 | 0.8 | 0.32727 | 0.8 | 0 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13333 | 0.5 | 0.1
2026-05-07 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0.3 | 0 | 0.2 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.3 | 0.275 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0
2026-05-07 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 | 0.125 | 0.2 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0
2026-05-07 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-07 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320