## PR_Calc
PR CALCULATION
08 MAGGIO 2026 | [67 empty] | 8 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 52
RAW PR | [64 empty] | 0.83404 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 83.4039
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 83.4611
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 83.401
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-08 | 00:00:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8257.1
2026-05-08 | 00:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 00:30:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 03:30:00.000 | -0.3 | -7.5e-05 | -0.1 | -2.5e-05 | -5e-05 | 0 | -5e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 03:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 04:00:00.000 | -1.9 | -0.000475 | -1.9 | -0.000475 | -0.000475 | 0 | -0.000475 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 04:15:00.000 | -1.9 | -0.000475 | -1.2 | -0.0003 | -0.0003875 | 0 | -0.0003875 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 04:30:00.000 | -1 | -0.00025 | -1.1 | -0.000275 | -0.0002625 | 0 | -0.0002625 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 04:45:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 05:00:00.000 | -1.3 | -0.000325 | -1.2 | -0.0003 | -0.0003125 | 0 | -0.0003125 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 05:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 05:30:00.000 | -1 | -0.00025 | -0.9 | -0.000225 | -0.0002375 | 0 | -0.0002375 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 05:45:00.000 | -0.2 | -5e-05 | -0.1 | -2.5e-05 | -3.75e-05 | 0 | -3.75e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 06:00:00.000 | 0 | 0 | 0.1 | 2.5e-05 | 1.25e-05 | 0 | 1.25e-05 | 0 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 06:15:00.000 | 3.5 | 0.000875 | 3.7 | 0.000925 | 0.0009 | 0 | 0.0009 | 0.055556 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 06:30:00.000 | 20.3 | 0.005075 | 20.6 | 0.00515 | 0.0051125 | 0 | 0.0051125 | 0.01467 | 30583.4 | 30583.4 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 06:45:00.000 | 50.7 | 0.012675 | 54.6 | 0.01365 | 0.013163 | 52.65 | 0.01365 | 0.074074 | 30583.4 | 30583.5 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24401 | 2.6841 | 0 | 2.6841 | 0.97294
2026-05-08 | 07:00:00.000 | 105 | 0.02625 | 106.5 | 0.026625 | 0.026437 | 105.75 | 0.026625 | 0.014184 | 30583.5 | 30583.6 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 07:15:00.000 | 112.4 | 0.0281 | 108.8 | 0.0272 | 0.02765 | 110.6 | 0.0281 | 0.03255 | 30583.6 | 30583.9 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 07:30:00.000 | 206.2 | 0.05155 | 199.1 | 0.049775 | 0.050662 | 202.65 | 0.05155 | 0.035036 | 30583.9 | 30584.3 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 07:45:00.000 | 108.2 | 0.02705 | 109.3 | 0.027325 | 0.027187 | 108.75 | 0.027325 | 0.010115 | 30584.3 | 30584.7 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 08:00:00.000 | 184.8 | 0.0462 | 187.2 | 0.0468 | 0.0465 | 186 | 0.0468 | 0.012903 | 30584.7 | 30585.1 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 08:15:00.000 | 237.6 | 0.0594 | 236.8 | 0.0592 | 0.0593 | 237.2 | 0.0594 | 0.0033727 | 30585.1 | 30585.8 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 08:30:00.000 | 155.6 | 0.0389 | 153.9 | 0.038475 | 0.038687 | 154.75 | 0.0389 | 0.010985 | 30585.8 | 30586.4 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 08:45:00.000 | 205.5 | 0.051375 | 203.3 | 0.050825 | 0.0511 | 204.4 | 0.051375 | 0.010763 | 30586.4 | 30586.9 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 09:00:00.000 | 462.2 | 0.11555 | 466 | 0.1165 | 0.11603 | 464.1 | 0.1165 | 0.0081879 | 30586.9 | 30587.7 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 09:15:00.000 | 841.5 | 0.21038 | 839.5 | 0.20988 | 0.21013 | 840.5 | 0.21038 | 0.0023795 | 30587.7 | 30589.7 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 09:30:00.000 | 874.1 | 0.21852 | 870.7 | 0.21768 | 0.2181 | 872.4 | 0.21852 | 0.0038973 | 30589.7 | 30592.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 09:45:00.000 | 797.4 | 0.19935 | 824.3 | 0.20607 | 0.20271 | 810.85 | 0.20607 | 0.033175 | 30592.1 | 30594.4 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 10:00:00.000 | 242.2 | 0.06055 | 253.3 | 0.063325 | 0.061938 | 247.75 | 0.063325 | 0.044803 | 30594.4 | 30595.9 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 10:15:00.000 | 312.8 | 0.0782 | 333.3 | 0.083325 | 0.080763 | 323.05 | 0.083325 | 0.063458 | 30595.9 | 30596.7 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 10:30:00.000 | 277.8 | 0.06945 | 290.5 | 0.072625 | 0.071038 | 284.15 | 0.072625 | 0.044695 | 30596.7 | 30597.7 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 10:45:00.000 | 379.6 | 0.0949 | 379.7 | 0.094925 | 0.094913 | 379.65 | 0.094925 | 0.0002634 | 30597.7 | 30598.8 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 11:00:00.000 | 254.2 | 0.06355 | 261.8 | 0.06545 | 0.0645 | 258 | 0.06545 | 0.029457 | 30598.8 | 30599.7 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 11:15:00.000 | 462.1 | 0.11553 | 507.5 | 0.12687 | 0.1212 | 484.8 | 0.12687 | 0.093647 | 30599.7 | 30600.8 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 11:30:00.000 | 504.8 | 0.1262 | 527.3 | 0.13182 | 0.12901 | 516.05 | 0.13182 | 0.0436 | 30600.8 | 30602.3 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 11:45:00.000 | 609.2 | 0.1523 | 642.9 | 0.16073 | 0.15651 | 626.05 | 0.16073 | 0.05383 | 30602.3 | 30603.9 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 12:00:00.000 | 1014.4 | 0.2536 | 994.5 | 0.24863 | 0.25111 | 1004.45 | 0.2536 | 0.019812 | 30603.9 | 30606 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 12:15:00.000 | 658.4 | 0.1646 | 637.1 | 0.15927 | 0.16194 | 647.75 | 0.1646 | 0.032883 | 30606 | 30608.2 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 12:30:00.000 | 958.1 | 0.23953 | 883.7 | 0.22093 | 0.23023 | 920.9 | 0.23953 | 0.080791 | 30608.2 | 30610.1 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 12:45:00.000 | 1048.8 | 0.2622 | 892.1 | 0.22303 | 0.24261 | 970.45 | 0.2622 | 0.16147 | 30610.1 | 30612.5 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 13:00:00.000 | 907.2 | 0.2268 | 962.1 | 0.24053 | 0.23366 | 934.65 | 0.24053 | 0.058739 | 30612.5 | 30614.7 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 13:15:00.000 | 963.4 | 0.24085 | 872 | 0.218 | 0.22942 | 917.7 | 0.24085 | 0.099597 | 30614.7 | 30616.9 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 13:30:00.000 | 1011.3 | 0.25282 | 984.3 | 0.24607 | 0.24945 | 997.8 | 0.25282 | 0.02706 | 30616.9 | 30619.3 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 13:45:00.000 | 924.3 | 0.23107 | 926.2 | 0.23155 | 0.23131 | 925.25 | 0.23155 | 0.0020535 | 30619.3 | 30621.8 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 14:00:00.000 | 844 | 0.211 | 850.9 | 0.21272 | 0.21186 | 847.45 | 0.21272 | 0.0081421 | 30621.8 | 30623.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 14:15:00.000 | 681.6 | 0.1704 | 668.4 | 0.1671 | 0.16875 | 675 | 0.1704 | 0.019556 | 30623.9 | 30625.7 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 14:30:00.000 | 674.4 | 0.1686 | 635.5 | 0.15887 | 0.16374 | 654.95 | 0.1686 | 0.059394 | 30625.7 | 30627.5 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 14:45:00.000 | 905.9 | 0.22647 | 948.6 | 0.23715 | 0.23181 | 927.25 | 0.23715 | 0.04605 | 30627.5 | 30629.2 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 15:00:00.000 | 992.9 | 0.24823 | 917.3 | 0.22933 | 0.23878 | 955.1 | 0.24823 | 0.079154 | 30629.2 | 30631.4 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 15:15:00.000 | 988.2 | 0.24705 | 978.1 | 0.24452 | 0.24579 | 983.15 | 0.24705 | 0.010273 | 30631.4 | 30633.8 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 15:30:00.000 | 1017.4 | 0.25435 | 974 | 0.2435 | 0.24893 | 995.7 | 0.25435 | 0.043587 | 30633.8 | 30636.2 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 15:45:00.000 | 1037.5 | 0.25938 | 986.4 | 0.2466 | 0.25299 | 1011.95 | 0.25938 | 0.050497 | 30636.2 | 30638.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 16:00:00.000 | 1003.6 | 0.2509 | 1012.6 | 0.25315 | 0.25202 | 1008.1 | 0.25315 | 0.0089277 | 30638.7 | 30641.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 16:15:00.000 | 602.8 | 0.1507 | 662 | 0.1655 | 0.1581 | 632.4 | 0.1655 | 0.093612 | 30641.1 | 30643 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 16:30:00.000 | 639.9 | 0.15998 | 490.1 | 0.12253 | 0.14125 | 565 | 0.15998 | 0.26513 | 30643 | 30644.7 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 16:45:00.000 | 514.9 | 0.12873 | 536.2 | 0.13405 | 0.13139 | 525.55 | 0.13405 | 0.040529 | 30644.7 | 30646.2 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 17:00:00.000 | 450.8 | 0.1127 | 327.8 | 0.08195 | 0.097325 | 389.3 | 0.1127 | 0.31595 | 30646.2 | 30647.6 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 17:15:00.000 | 314.3 | 0.078575 | 323.5 | 0.080875 | 0.079725 | 318.9 | 0.080875 | 0.028849 | 30647.6 | 30648.4 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 17:30:00.000 | 666.2 | 0.16655 | 689 | 0.17225 | 0.1694 | 677.6 | 0.17225 | 0.033648 | 30648.4 | 30649.5 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 17:45:00.000 | 831.8 | 0.20795 | 880.4 | 0.2201 | 0.21402 | 856.1 | 0.2201 | 0.056769 | 30649.5 | 30651.7 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 18:00:00.000 | 447.3 | 0.11183 | 457.6 | 0.1144 | 0.11311 | 452.45 | 0.1144 | 0.022765 | 30651.7 | 30653.6 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 18:15:00.000 | 262.1 | 0.065525 | 275.2 | 0.0688 | 0.067162 | 268.65 | 0.0688 | 0.048762 | 30653.6 | 30654.3 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 18:30:00.000 | 289.3 | 0.072325 | 289 | 0.07225 | 0.072288 | 289.15 | 0.072325 | 0.0010375 | 30654.3 | 30655.2 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 18:45:00.000 | 282.7 | 0.070675 | 350.9 | 0.087725 | 0.0792 | 316.8 | 0.087725 | 0.21528 | 30655.2 | 30656 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 19:00:00.000 | 209.2 | 0.0523 | 264.8 | 0.0662 | 0.05925 | 237 | 0.0662 | 0.2346 | 30656 | 30656.8 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 19:15:00.000 | 124.4 | 0.0311 | 164.5 | 0.041125 | 0.036113 | 144.45 | 0.041125 | 0.2776 | 30656.8 | 30657.3 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 19:30:00.000 | 59.5 | 0.014875 | 88.5 | 0.022125 | 0.0185 | 74 | 0.022125 | 0.39189 | 30657.3 | 30657.5 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 19:45:00.000 | 25.7 | 0.006425 | 40.7 | 0.010175 | 0.0083 | 0 | 0.0083 | 0.45181 | 30657.5 | 30657.6 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 20:00:00.000 | 8.6 | 0.00215 | 8.7 | 0.002175 | 0.0021625 | 0 | 0.0021625 | 0.011561 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 20:15:00.000 | 1.4 | 0.00035 | 1.6 | 0.0004 | 0.000375 | 0 | 0.000375 | 0.13333 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 20:30:00.000 | -1.4 | -0.00035 | -1.3 | -0.000325 | -0.0003375 | 0 | -0.0003375 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 20:45:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 21:00:00.000 | -1.7 | -0.000425 | -1.5 | -0.000375 | -0.0004 | 0 | -0.0004 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 21:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 21:30:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 21:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 22:00:00.000 | -1.3 | -0.000325 | -1 | -0.00025 | -0.0002875 | 0 | -0.0002875 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 22:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 22:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 22:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 23:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 23:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 23:30:00.000 | -1.4 | -0.00035 | -1 | -0.00025 | -0.0003 | 0 | -0.0003 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
2026-05-08 | 23:45:00.000 | -2 | -0.0005 | -1.3 | -0.000325 | -0.0004125 | 0 | -0.0004125 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97294
PR for each inverter |  |  | 7.1846 |  | 7.1323 | 7.1585 |  | 7.3589 |  |  |  | 74200 |  | 0.84003 | 0.83831 | 0.84401 | 0.85387 | 0.85153 | 0.84434 | 0.85443 | 0.83626 | 0.82731 | 0.83139 | 0.82843 | 0.85935 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.87622 | 0.8574 | 0.85142 | 0.87288 | 0.87677 | 0.83243 | 0.84934 | 0.82817 | 0.82661 | 0.84669 | 0.82653 | 0.82194 |  |  |  | 0 | 0.83402 | 0.83097 | 0.67739 | 0.82287 | 0.81674 | 0.82129 | 0.82252 | 0.81183 | 0.81965 | 0.82238 | 0.83476 | 0.85592 | #DIV/0! | #DIV/0! | #DIV/0! | 2.6841 |  | 0.83461 |  | #DIV/0! | #DIV/0! | 8.8929e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-08 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 06:30:00.000 | 2 | 1.8 | 2.6 | 2.3 | 3.4 | 2.2 | 2.5 | 2.4 | 2.6 | 2.3 | 2.5 | 2.9 | 2.4583 | 3.4 | 1.8 | 2.5 | 2.2 | 4.3 | 2.5 | 3.9 | 2.6 | 2.8 | 4.2 | 2.8 | 2.4 | 2.5 | 4.1 | 3.0667 | 4.3 | 2.2 | 3.6 | 2 | 0 | 2.5 | 2.5 | 2.5 | 2.6 | 2.4 | 2.4 | 2.4 | 2.9 | 2.6 | 2.5818 | 3.6 | 0
2026-05-08 | 06:45:00.000 | 3.2 | 3.7 | 11.2 | 11.3 | 2.3 | 11.1 | 11 | 11.1 | 11.5 | 11.2 | 11.5 | 11.6 | 9.225 | 11.6 | 2.3 | 10.4 | 10.5 | 11.5 | 11 | 10.8 | 11.3 | 11.5 | 11.9 | 11.9 | 11.2 | 12.1 | 12.2 | 11.3583 | 12.2 | 10.4 | 11.7 | 10.4 | 0 | 11.7 | 11.5 | 12.2 | 3.3 | 11.7 | 11.5 | 10.9 | 12.1 | 11.1 | 10.7364 | 12.2 | 0
2026-05-08 | 07:00:00.000 | 21.8 | 21.2 | 25.8 | 25.9 | 25.4 | 25.2 | 24.9 | 25.1 | 25.7 | 25.8 | 26.5 | 25.9 | 24.9333 | 26.5 | 21.2 | 23.8 | 23.3 | 24.3 | 25 | 24.5 | 25.8 | 25.6 | 26.4 | 27.1 | 25.3 | 27.1 | 26.3 | 25.375 | 27.1 | 23.3 | 27 | 24.1 | 0.1 | 26.6 | 26.6 | 28 | 25.7 | 26.7 | 26 | 24.4 | 26.9 | 25.8 | 23.9917 | 28 | 0.1
2026-05-08 | 07:15:00.000 | 30.4 | 30 | 31.6 | 31.3 | 31.7 | 31.2 | 30.5 | 31.9 | 32 | 32.1 | 32.9 | 32 | 31.4667 | 32.9 | 30 | 29.4 | 29.6 | 30.4 | 29.9 | 30.5 | 32.2 | 31.6 | 32.6 | 33.4 | 31.6 | 33.8 | 33.4 | 31.5333 | 33.8 | 29.4 | 32.5 | 30.1 | 0.1 | 32.1 | 31 | 32.4 | 32.6 | 31.7 | 31.6 | 30.9 | 33.3 | 29.9 | 29.0167 | 33.3 | 0.1
2026-05-08 | 07:30:00.000 | 63.9 | 63.2 | 65.1 | 65.1 | 65.2 | 64.2 | 63.8 | 66.4 | 66.2 | 66 | 67 | 65.4 | 65.125 | 67 | 63.2 | 60.8 | 61.8 | 62.5 | 62.2 | 61.8 | 66.2 | 64.2 | 66.5 | 67.2 | 63.6 | 67.4 | 66.8 | 64.25 | 67.4 | 60.8 | 66.1 | 65.8 | 0.1 | 68.8 | 68.4 | 69.8 | 69 | 66.2 | 67.1 | 65.2 | 68.9 | 63.7 | 61.5917 | 69.8 | 0.1
2026-05-08 | 07:45:00.000 | 35.7 | 35.3 | 35.7 | 36.3 | 36 | 35.8 | 36.1 | 37.9 | 37.4 | 37.1 | 37.2 | 36.6 | 36.425 | 37.9 | 35.3 | 34.3 | 36 | 35.6 | 34.4 | 34.4 | 37.7 | 36.1 | 37.3 | 37.3 | 35.7 | 37.3 | 37.6 | 36.1417 | 37.7 | 34.3 | 37.5 | 37.1 | 0.1 | 37.3 | 37.2 | 37 | 37.4 | 36.6 | 36.9 | 36.9 | 37.5 | 33.9 | 33.7833 | 37.5 | 0.1
2026-05-08 | 08:00:00.000 | 59.4 | 59.1 | 60.2 | 61.2 | 57.6 | 60.9 | 60.9 | 63.2 | 63 | 62.5 | 62.6 | 62.1 | 61.0583 | 63.2 | 57.6 | 57.9 | 60.6 | 60.1 | 58.6 | 58.7 | 64 | 60.8 | 63.6 | 63.8 | 60.7 | 63.6 | 64 | 61.3667 | 64 | 57.9 | 64.4 | 62.7 | 0.1 | 63.4 | 62.9 | 62.7 | 63.5 | 62.1 | 62.6 | 62.2 | 64.4 | 57.2 | 57.35 | 64.4 | 0.1
2026-05-08 | 08:15:00.000 | 79.8 | 78.8 | 79.5 | 81.1 | 80.4 | 80.1 | 79.9 | 83.5 | 81.8 | 82 | 81.8 | 80.1 | 80.7333 | 83.5 | 78.8 | 76.5 | 79.4 | 79.5 | 76.1 | 76.5 | 82.7 | 78.2 | 81.3 | 80.5 | 76.5 | 79.7 | 80.1 | 78.9167 | 82.7 | 76.1 | 80.6 | 80.2 | 0.1 | 81.6 | 81.1 | 80.6 | 82.8 | 81.5 | 81.7 | 81.2 | 82.2 | 75.1 | 74.0583 | 82.8 | 0.1
2026-05-08 | 08:30:00.000 | 54 | 53.1 | 53.5 | 54.7 | 54.1 | 53.8 | 54.7 | 57.4 | 56.2 | 55.6 | 55.6 | 54.7 | 54.7833 | 57.4 | 53.1 | 51.8 | 54.5 | 53.8 | 51.5 | 51.6 | 56.2 | 53.6 | 55.4 | 55 | 52.5 | 54.6 | 55.2 | 53.8083 | 56.2 | 51.5 | 55.3 | 55.4 | 0.1 | 55.3 | 55.1 | 54.4 | 55.5 | 54 | 54.6 | 54.9 | 55.4 | 50.7 | 50.0583 | 55.5 | 0.1
2026-05-08 | 08:45:00.000 | 69.1 | 68.1 | 68.9 | 70.4 | 69.8 | 69.7 | 70.9 | 74 | 72.8 | 72 | 72.1 | 71.1 | 70.7417 | 74 | 68.1 | 67.5 | 70.9 | 70 | 67.2 | 67.5 | 73.4 | 70 | 72.5 | 72 | 68.9 | 71.8 | 72.7 | 70.3667 | 73.4 | 67.2 | 71.7 | 71.7 | 0.1 | 71.3 | 70.7 | 69.7 | 70.9 | 69.1 | 69.9 | 70.5 | 71.4 | 64.2 | 64.2667 | 71.7 | 0.1
2026-05-08 | 09:00:00.000 | 148.1 | 146.1 | 146 | 146.8 | 142.4 | 148.3 | 151 | 157.6 | 157.2 | 154.7 | 153.2 | 150.9 | 150.1917 | 157.6 | 142.4 | 143.8 | 153.4 | 150.4 | 146.8 | 143.8 | 161.3 | 152.2 | 157.3 | 153.1 | 147 | 154.8 | 155.2 | 151.5917 | 161.3 | 143.8 | 158.8 | 158.7 | 0.1 | 153.5 | 149.1 | 156.6 | 155.6 | 146.8 | 145.5 | 147 | 159.3 | 137.8 | 139.0667 | 159.3 | 0.1
2026-05-08 | 09:15:00.000 | 266.1 | 262.9 | 265.3 | 267.9 | 266.4 | 266.3 | 269.5 | 281.1 | 278.1 | 275.9 | 276 | 269.8 | 270.4417 | 281.1 | 262.9 | 255.8 | 267.2 | 264.4 | 254.6 | 255.9 | 278.9 | 264.5 | 274.8 | 272.8 | 261.4 | 272.2 | 274.7 | 266.4333 | 278.9 | 254.6 | 278 | 276.7 | 0.1 | 279 | 277.8 | 276.5 | 279.4 | 271.9 | 273.7 | 274.9 | 277.9 | 253.5 | 251.6167 | 279.4 | 0.1
2026-05-08 | 09:30:00.000 | 272.4 | 268.8 | 271.1 | 273.6 | 272.1 | 271.7 | 275.2 | 281.3 | 281 | 280.5 | 280.4 | 275.6 | 275.3083 | 281.3 | 268.8 | 260.4 | 272.2 | 269.5 | 259.7 | 261.1 | 281.3 | 270.3 | 280.1 | 279.1 | 267.6 | 278.6 | 280.1 | 271.6667 | 281.3 | 259.7 | 281.2 | 281 | 0.1 | 281.2 | 281.4 | 281.1 | 281.4 | 278.3 | 279.5 | 270.2 | 281.2 | 259.7 | 254.6917 | 281.4 | 0.1
2026-05-08 | 09:45:00.000 | 250.5 | 251.1 | 246.7 | 261.1 | 260.4 | 259.2 | 260.4 | 266.4 | 266 | 266.2 | 254.9 | 263.6 | 258.875 | 266.4 | 246.7 | 251.4 | 258.5 | 256.4 | 249.5 | 249.9 | 258 | 260.5 | 263.5 | 262 | 256.6 | 260 | 260.4 | 257.225 | 263.5 | 249.5 | 281.1 | 281.2 | 0.1 | 281.1 | 281.6 | 281.5 | 251.3 | 250.2 | 254.7 | 260 | 281.2 | 225.2 | 244.1 | 281.6 | 0.1
2026-05-08 | 10:00:00.000 | 86.5 | 84.4 | 85 | 87.2 | 86.4 | 85.7 | 87.8 | 93.4 | 91.2 | 90.4 | 90.2 | 89.4 | 88.1333 | 93.4 | 84.4 | 84.4 | 88 | 87 | 83 | 83.7 | 93.7 | 89.3 | 93.1 | 92.4 | 88.2 | 90.9 | 93.9 | 88.9667 | 93.9 | 83 | 128 | 130.3 | 40.4 | 131.2 | 130.5 | 130.3 | 92.9 | 89.8 | 90.4 | 91.3 | 128.9 | 83.9 | 105.6583 | 131.2 | 40.4
2026-05-08 | 10:15:00.000 | 105.8 | 104.9 | 105.6 | 109.1 | 109.7 | 109.5 | 112 | 118.6 | 113 | 118.8 | 118.6 | 117.7 | 111.9417 | 118.8 | 104.9 | 107.4 | 113.2 | 112.7 | 107.5 | 109.6 | 125.5 | 120 | 123.6 | 124.2 | 121.7 | 125.3 | 129.1 | 118.3167 | 129.1 | 107.4 | 124.4 | 120.1 | 117.2 | 117.5 | 116.1 | 112.5 | 114.3 | 110.7 | 112.6 | 114.5 | 118.5 | 95.4 | 114.4833 | 124.4 | 95.4
2026-05-08 | 10:30:00.000 | 98.8 | 96.8 | 97.4 | 99 | 97.8 | 96.5 | 98 | 107.3 | 105.8 | 103.4 | 103.9 | 101.2 | 100.4917 | 107.3 | 96.5 | 93.8 | 98.5 | 96.6 | 92.5 | 93.3 | 106.3 | 99.9 | 104.3 | 102.4 | 98.3 | 102.2 | 103.4 | 99.2917 | 106.3 | 92.5 | 105.6 | 106.2 | 98.7 | 105.6 | 102.9 | 101.3 | 105.4 | 101.8 | 103.1 | 104.3 | 106.4 | 93.9 | 102.9333 | 106.4 | 93.9
2026-05-08 | 10:45:00.000 | 131.2 | 128.7 | 128.2 | 131.3 | 129.4 | 128.3 | 129.6 | 138.9 | 136.3 | 133.4 | 133.1 | 129.9 | 131.525 | 138.9 | 128.2 | 123.3 | 129.6 | 127.7 | 117.9 | 122.9 | 133.1 | 126.7 | 134.3 | 130.2 | 124.4 | 128.8 | 129.9 | 127.4 | 134.3 | 117.9 | 134 | 136.2 | 133.8 | 136.9 | 130.5 | 134.2 | 138.2 | 134.3 | 136.3 | 136.8 | 134.4 | 126.3 | 134.325 | 138.2 | 126.3
2026-05-08 | 11:00:00.000 | 83.6 | 88.8 | 89.5 | 91.8 | 91 | 90.2 | 92 | 97.1 | 95 | 94.2 | 93.8 | 92.6 | 91.6333 | 97.1 | 83.6 | 87.4 | 92.1 | 90.9 | 87 | 87.5 | 95.7 | 91.3 | 95.3 | 93.9 | 90 | 93.5 | 95.2 | 91.65 | 95.7 | 87 | 95 | 95.1 | 98.4 | 94.6 | 93.9 | 92.4 | 95.1 | 93.5 | 94.1 | 93.8 | 94.6 | 85.8 | 93.8583 | 98.4 | 85.8
2026-05-08 | 11:15:00.000 | 115.3 | 150.9 | 149.8 | 153.5 | 151.9 | 152 | 153.1 | 163.6 | 161.1 | 161.9 | 159.9 | 161.1 | 152.8417 | 163.6 | 115.3 | 146.2 | 154.6 | 152.6 | 146.7 | 146.2 | 165.7 | 159.4 | 163.6 | 161.4 | 158.5 | 162.1 | 166.2 | 156.9333 | 166.2 | 146.2 | 165.1 | 165.6 | 161.9 | 163.8 | 152.9 | 158.9 | 163.5 | 159.8 | 160.5 | 160.9 | 164.3 | 146.7 | 160.325 | 165.6 | 146.7
2026-05-08 | 11:30:00.000 | 166.8 | 165.9 | 165.3 | 168.8 | 165.7 | 165.5 | 167.5 | 179.7 | 176.5 | 175.6 | 174.5 | 171.6 | 170.2833 | 179.7 | 165.3 | 159.7 | 168.5 | 160.5 | 159.9 | 160 | 178.5 | 170.6 | 178.7 | 177.5 | 168.5 | 174.9 | 178.4 | 169.6417 | 178.7 | 159.7 | 181.9 | 177 | 178.3 | 176.6 | 176 | 174.1 | 179.5 | 166.9 | 174.1 | 174.4 | 179.1 | 162.5 | 175.0333 | 181.9 | 162.5
2026-05-08 | 11:45:00.000 | 182.2 | 180.9 | 186.2 | 186 | 188.5 | 186.9 | 191.5 | 194.3 | 201.6 | 194.4 | 191 | 194.8 | 189.8583 | 201.6 | 180.9 | 182.5 | 190.7 | 188.3 | 184.8 | 186.2 | 208.2 | 194.2 | 204 | 192.7 | 194.7 | 196.4 | 212.2 | 194.575 | 212.2 | 182.5 | 199.3 | 202.2 | 203.7 | 199.3 | 190.1 | 191.9 | 199.3 | 194.7 | 196.8 | 198.9 | 205.2 | 179.6 | 196.75 | 205.2 | 179.6
2026-05-08 | 12:00:00.000 | 266.4 | 265.2 | 268.1 | 267.5 | 268.8 | 209.9 | 267.6 | 268.4 | 267.4 | 270.5 | 266.5 | 269.4 | 262.975 | 270.5 | 209.9 | 266.2 | 269.2 | 266.4 | 265.6 | 256.7 | 267.6 | 259.9 | 270.5 | 269.1 | 265.4 | 265.4 | 255.7 | 264.8083 | 270.5 | 255.7 | 273.7 | 273.8 | 269.9 | 274.5 | 270 | 269.7 | 265.5 | 273 | 271.9 | 273.2 | 272.5 | 267.9 | 271.3 | 274.5 | 265.5
2026-05-08 | 12:15:00.000 | 198.3 | 197.8 | 196.8 | 199.3 | 199.6 | 184.3 | 199.4 | 203.2 | 201.2 | 200.2 | 199.7 | 197.4 | 198.1 | 203.2 | 184.3 | 193.5 | 199.2 | 197.6 | 192.2 | 193.3 | 199.1 | 192.8 | 201.2 | 198.9 | 193.2 | 200.1 | 195.4 | 196.375 | 201.2 | 192.2 | 180.3 | 199.1 | 198.3 | 199.8 | 199.6 | 198 | 197.7 | 194.7 | 195.7 | 195.5 | 198.8 | 190.7 | 195.6833 | 199.8 | 180.3
2026-05-08 | 12:30:00.000 | 267 | 266.3 | 264.7 | 263 | 268.3 | 266.3 | 266.6 | 262.1 | 210.2 | 258.1 | 261.2 | 255.6 | 259.1167 | 268.3 | 210.2 | 260.7 | 263.7 | 259.4 | 260.5 | 254.7 | 254.1 | 246.9 | 238.6 | 244.6 | 249.6 | 254.6 | 242.1 | 252.4583 | 263.7 | 238.6 | 243.1 | 247.2 | 247.1 | 244 | 241.8 | 243.6 | 258.4 | 256.3 | 255.4 | 253.9 | 249.6 | 266.6 | 250.5833 | 266.6 | 241.8
2026-05-08 | 12:45:00.000 | 281.1 | 280.4 | 281.5 | 280.7 | 280.4 | 281.4 | 279.9 | 276.7 | 272.6 | 274 | 273.7 | 273.1 | 277.9583 | 281.5 | 272.6 | 270.6 | 278.9 | 271.2 | 268.4 | 280.4 | 261.4 | 258.2 | 257.5 | 255.6 | 252.7 | 260.4 | 246.9 | 263.5167 | 280.4 | 246.9 | 243 | 246.6 | 249 | 247.9 | 256 | 261.3 | 271 | 269.6 | 264.2 | 267 | 266.8 | 272.9 | 259.6083 | 272.9 | 243
2026-05-08 | 13:00:00.000 | 244.6 | 246.3 | 244.8 | 245.6 | 248.6 | 248.5 | 250.7 | 241.2 | 248.5 | 251.4 | 248.4 | 253.7 | 247.6917 | 253.7 | 241.2 | 248 | 251.9 | 249.3 | 248.5 | 246.8 | 262.6 | 264.3 | 270 | 271.3 | 270 | 270.2 | 275.8 | 260.725 | 275.8 | 246.8 | 271.7 | 268.9 | 268.6 | 265.1 | 266.9 | 262.4 | 251.5 | 252.2 | 253.1 | 251 | 257.1 | 239.8 | 259.025 | 271.7 | 239.8
2026-05-08 | 13:15:00.000 | 262.3 | 260.7 | 254.9 | 258.6 | 259.8 | 253.7 | 259.4 | 254.9 | 252.4 | 255 | 252.3 | 254.5 | 256.5417 | 262.3 | 252.3 | 251.8 | 255.1 | 251 | 247.9 | 248 | 253.5 | 249.9 | 246.5 | 248.2 | 248.2 | 252 | 246 | 249.8417 | 255.1 | 246 | 239.3 | 237.5 | 232.2 | 243.5 | 232.9 | 242 | 251 | 252 | 250.4 | 248.6 | 248.9 | 260.5 | 244.9 | 260.5 | 232.2
2026-05-08 | 13:30:00.000 | 281.1 | 281.4 | 281.2 | 281.2 | 281 | 281.4 | 281.2 | 280.3 | 279.3 | 277.8 | 279.2 | 277.8 | 280.2417 | 281.4 | 277.8 | 279.5 | 279.6 | 281.3 | 280 | 271.1 | 277.7 | 278.9 | 280.3 | 279.7 | 280.6 | 281.1 | 281.3 | 279.2583 | 281.3 | 271.1 | 281.4 | 281.6 | 281.6 | 281.5 | 281.7 | 281.4 | 278.3 | 277.7 | 277.2 | 278 | 277.1 | 271.7 | 279.1 | 281.7 | 271.7
2026-05-08 | 13:45:00.000 | 257.6 | 253.7 | 246.8 | 255.2 | 242.8 | 254.8 | 249.4 | 254.6 | 249.6 | 261.6 | 263 | 260.5 | 254.1333 | 263 | 242.8 | 251.2 | 253.4 | 250.5 | 239.6 | 250.4 | 262.4 | 260.7 | 259.8 | 258.1 | 241.5 | 255.1 | 252.5 | 252.9333 | 262.4 | 239.6 | 258.6 | 262 | 261.9 | 265 | 266.1 | 265.3 | 260.1 | 258.3 | 259.3 | 261 | 258.8 | 235.5 | 259.325 | 266.1 | 235.5
2026-05-08 | 14:00:00.000 | 231 | 223.4 | 233.2 | 235.4 | 226.9 | 229.2 | 223 | 230.5 | 234.6 | 233.3 | 231.9 | 233.1 | 230.4583 | 235.4 | 223 | 224 | 216.9 | 227.5 | 225.5 | 226.6 | 231.6 | 227.5 | 227.8 | 226.3 | 222.4 | 224.8 | 220.6 | 225.125 | 231.6 | 216.9 | 233.8 | 236.2 | 235.7 | 239.2 | 233.6 | 242.2 | 237.8 | 241.2 | 230.3 | 242.1 | 234 | 216.9 | 235.25 | 242.2 | 216.9
2026-05-08 | 14:15:00.000 | 198.8 | 190.8 | 199.1 | 197.1 | 202.1 | 198.3 | 206.3 | 185.2 | 187.3 | 187.4 | 183.8 | 191.2 | 193.95 | 206.3 | 183.8 | 196.4 | 201.1 | 204.5 | 194.9 | 202 | 200.7 | 199.2 | 202.7 | 206.3 | 202.9 | 204.4 | 210.5 | 202.1333 | 210.5 | 194.9 | 194.9 | 190.8 | 184.7 | 168 | 187 | 184.5 | 173.2 | 167.6 | 179.1 | 181 | 176.2 | 177.5 | 180.375 | 194.9 | 167.6
2026-05-08 | 14:30:00.000 | 177.4 | 175.8 | 176.5 | 182.1 | 177.5 | 185.5 | 179.2 | 184.4 | 183.5 | 179.9 | 182.6 | 179 | 180.2833 | 185.5 | 175.8 | 174 | 173.9 | 181 | 174.3 | 173.2 | 183.5 | 172.7 | 176.4 | 184.5 | 178.6 | 179.1 | 179.7 | 177.575 | 184.5 | 172.7 | 185.6 | 185.1 | 191.1 | 188.4 | 189.7 | 187.3 | 186 | 183.6 | 183 | 179 | 185.9 | 169.4 | 184.5083 | 191.1 | 169.4
2026-05-08 | 14:45:00.000 | 229.5 | 228.7 | 229.7 | 233 | 233.1 | 226.7 | 238.3 | 246.2 | 249.9 | 252.6 | 250 | 240.7 | 238.2 | 252.6 | 226.7 | 243.9 | 247.3 | 246.2 | 243.9 | 249.1 | 255.7 | 254.8 | 259.8 | 253.6 | 256.6 | 260.2 | 254.1 | 252.1 | 260.2 | 243.9 | 254.4 | 251 | 246.2 | 249.7 | 238.2 | 238.7 | 232.9 | 234.5 | 237.7 | 242.9 | 249.9 | 202.8 | 239.9083 | 254.4 | 202.8
2026-05-08 | 15:00:00.000 | 254.9 | 251.2 | 248.2 | 244.2 | 240.8 | 240.2 | 240.2 | 257.4 | 250.8 | 247 | 248.5 | 244.7 | 247.3417 | 257.4 | 240.2 | 240.4 | 242.7 | 242.3 | 240.4 | 240 | 242.9 | 239.5 | 239.7 | 240.4 | 239.4 | 241.9 | 228 | 239.8 | 242.9 | 228 | 245.5 | 244.1 | 247.4 | 247.2 | 248.1 | 246.7 | 258.1 | 246.8 | 248.9 | 245.3 | 251.7 | 264.1 | 249.4917 | 264.1 | 244.1
2026-05-08 | 15:15:00.000 | 267.6 | 266.5 | 265.1 | 267 | 266.1 | 269.7 | 270.9 | 274.7 | 275.2 | 273.9 | 274.4 | 274.5 | 270.4667 | 275.2 | 265.1 | 273.5 | 275.8 | 272.1 | 275.4 | 274.2 | 279.3 | 280.1 | 280.9 | 281.3 | 281.6 | 281 | 281.5 | 278.0583 | 281.6 | 272.1 | 281.2 | 281.3 | 281.2 | 281 | 281.2 | 278.5 | 273.2 | 272.8 | 273.1 | 272.8 | 274.7 | 269.5 | 276.7083 | 281.3 | 269.5
2026-05-08 | 15:30:00.000 | 281.3 | 281.1 | 281.2 | 279.9 | 279.5 | 278.3 | 277.1 | 281.2 | 281.1 | 281.2 | 281.1 | 281.3 | 280.3583 | 281.3 | 277.1 | 279 | 279.3 | 277.6 | 278.4 | 278.4 | 281.3 | 281.3 | 281.1 | 281.3 | 281.6 | 281 | 281.5 | 280.15 | 281.6 | 277.6 | 281.1 | 281.4 | 281.2 | 270.7 | 281.1 | 281.1 | 276.5 | 277.4 | 278.9 | 277.4 | 279 | 274.6 | 278.3667 | 281.4 | 270.7
2026-05-08 | 15:45:00.000 | 281.7 | 281 | 281.2 | 280.9 | 281.4 | 281.4 | 281.2 | 281.3 | 279.4 | 280.2 | 279.4 | 280.7 | 280.8167 | 281.7 | 279.4 | 281.1 | 280.9 | 281.2 | 281.2 | 281.2 | 281 | 280.1 | 275.1 | 280.2 | 281.2 | 280.4 | 277.6 | 280.1 | 281.2 | 275.1 | 272.6 | 271 | 271.9 | 271.8 | 271.3 | 275.2 | 275.9 | 274.7 | 275.6 | 275.6 | 273.3 | 280.7 | 274.1333 | 280.7 | 271
2026-05-08 | 16:00:00.000 | 269 | 264.6 | 264.9 | 258.2 | 260 | 260.7 | 260.1 | 269.2 | 267.7 | 272.1 | 271.5 | 263.4 | 265.1167 | 272.1 | 258.2 | 266.6 | 268.3 | 262.8 | 262.6 | 259 | 275.9 | 276.7 | 278.3 | 277 | 276.6 | 279.1 | 278.3 | 271.7667 | 279.1 | 259 | 277.5 | 278.1 | 276.2 | 277.7 | 274.2 | 275.9 | 277.8 | 276.1 | 277.9 | 277.8 | 274.6 | 277.7 | 276.7917 | 278.1 | 274.2
2026-05-08 | 16:15:00.000 | 156.3 | 155.6 | 162 | 158.9 | 169.2 | 181.1 | 186.7 | 166.5 | 167 | 164.5 | 170 | 172.2 | 167.5 | 186.7 | 155.6 | 187 | 195.5 | 194.2 | 195.1 | 197.8 | 173.9 | 174.3 | 180.8 | 181.6 | 185.1 | 194.1 | 187.6 | 187.25 | 197.8 | 173.9 | 175.2 | 176.1 | 173.1 | 170.4 | 176 | 185.4 | 182.3 | 179.7 | 173.4 | 174.5 | 176.2 | 165.8 | 175.675 | 185.4 | 165.8
2026-05-08 | 16:30:00.000 | 172.6 | 178.9 | 194.4 | 215.9 | 225.9 | 226.5 | 243.2 | 176.7 | 182.7 | 186 | 193.9 | 197.7 | 199.5333 | 243.2 | 172.6 | 240.8 | 250.9 | 251.5 | 254.6 | 255.4 | 185.2 | 183.3 | 194.9 | 200.1 | 204.7 | 221.6 | 199.5 | 220.2083 | 255.4 | 183.3 | 151.5 | 131.5 | 130.2 | 124.1 | 118.2 | 117.6 | 128 | 132 | 140.1 | 139.7 | 150.1 | 129.3 | 132.6917 | 151.5 | 117.6
2026-05-08 | 16:45:00.000 | 146.9 | 144.4 | 142.3 | 145.7 | 146.1 | 146.7 | 141.6 | 157.8 | 155.5 | 170.8 | 162.7 | 176.4 | 153.075 | 176.4 | 141.6 | 151.3 | 158.3 | 157.5 | 154 | 149.9 | 192 | 185.3 | 189.6 | 182.6 | 172.5 | 166.1 | 164.9 | 168.6667 | 192 | 149.9 | 176.3 | 153.6 | 150 | 142.8 | 125.2 | 125.7 | 133.3 | 138.3 | 149.5 | 158.1 | 178.5 | 126.9 | 146.5167 | 178.5 | 125.2
2026-05-08 | 17:00:00.000 | 119.8 | 126 | 128.7 | 130.4 | 128.8 | 121.9 | 121.5 | 125.1 | 122.6 | 116.6 | 114.8 | 107.5 | 121.975 | 130.4 | 107.5 | 114 | 115.4 | 111.7 | 110.3 | 108.7 | 96.9 | 90.5 | 86.1 | 93.4 | 92.3 | 98 | 88.4 | 100.475 | 115.4 | 86.1 | 95 | 96.2 | 96.5 | 98.3 | 98.9 | 108.4 | 120.8 | 118.1 | 118.1 | 113.2 | 101.1 | 138.4 | 108.5833 | 138.4 | 95
2026-05-08 | 17:15:00.000 | 89.9 | 86.8 | 93.4 | 96.7 | 100 | 101.7 | 104.1 | 105.3 | 106.8 | 105.6 | 105.5 | 103.7 | 99.9583 | 106.8 | 86.8 | 100.8 | 104.2 | 104.5 | 101.2 | 103.6 | 102.9 | 98.1 | 104 | 104.2 | 102.1 | 101.3 | 106.5 | 102.7833 | 106.5 | 98.1 | 102.1 | 102.4 | 97 | 98.9 | 101.8 | 103.9 | 100.5 | 97.7 | 99 | 99.6 | 101.5 | 80.3 | 98.725 | 103.9 | 80.3
2026-05-08 | 17:30:00.000 | 198.3 | 197.8 | 197.9 | 199.1 | 197.2 | 198.5 | 199.5 | 203.3 | 203.9 | 202.7 | 204.3 | 202.1 | 200.3833 | 204.3 | 197.2 | 192.9 | 198.5 | 199 | 193.5 | 196.7 | 204.5 | 201 | 204.4 | 206.5 | 201 | 207.6 | 195.3 | 200.075 | 207.6 | 192.9 | 204.5 | 201.5 | 200.7 | 202.3 | 201.2 | 203.4 | 200.8 | 199.4 | 200.1 | 199.1 | 193.2 | 189 | 199.6 | 204.5 | 189
2026-05-08 | 17:45:00.000 | 256.4 | 254.8 | 255.2 | 256.1 | 255.6 | 252.6 | 242.3 | 274.8 | 273 | 270.1 | 269.3 | 256.1 | 259.6917 | 274.8 | 242.3 | 223 | 225.1 | 218.7 | 205.2 | 210.1 | 260.8 | 246.7 | 252.5 | 251.2 | 238.1 | 241 | 244 | 234.7 | 260.8 | 205.2 | 276.2 | 274.2 | 269.7 | 252.5 | 250.3 | 244.5 | 256.5 | 248.1 | 264.6 | 261.3 | 274.3 | 234.1 | 258.8583 | 276.2 | 234.1
2026-05-08 | 18:00:00.000 | 146.1 | 145.7 | 146.6 | 150.6 | 148.3 | 141.8 | 127.7 | 150.4 | 147.3 | 144.4 | 135.9 | 136.9 | 143.475 | 150.6 | 127.7 | 126.5 | 130.8 | 127.6 | 120.6 | 123.2 | 133.3 | 126.9 | 127.8 | 126.5 | 120.4 | 122 | 125.4 | 125.9167 | 133.3 | 120.4 | 139.7 | 145.8 | 149.9 | 154.1 | 153.3 | 154.6 | 160.3 | 151.2 | 149.9 | 149.4 | 143.9 | 155.1 | 150.6 | 160.3 | 139.7
2026-05-08 | 18:15:00.000 | 75.9 | 73.9 | 72.6 | 73.6 | 72.2 | 68.5 | 65.2 | 86.3 | 83 | 81.4 | 79 | 74.3 | 75.4917 | 86.3 | 65.2 | 64.8 | 67.9 | 66.8 | 64.3 | 66.4 | 80 | 77.2 | 80.6 | 82 | 79.2 | 81.8 | 88.3 | 74.9417 | 88.3 | 64.3 | 90.7 | 88.9 | 85.8 | 84.5 | 81.2 | 81.4 | 89.8 | 85.9 | 87.3 | 89.4 | 89.6 | 82.7 | 86.4333 | 90.7 | 81.2
2026-05-08 | 18:30:00.000 | 95.6 | 96.1 | 95.6 | 97.2 | 97 | 97.4 | 98.9 | 102.8 | 100.8 | 97.4 | 98.3 | 94.5 | 97.6333 | 102.8 | 94.5 | 96.1 | 103.6 | 103.1 | 98.6 | 98.6 | 92.2 | 91 | 94.5 | 95.3 | 91.2 | 92.8 | 92.9 | 95.825 | 103.6 | 91 | 92.4 | 88.7 | 81.7 | 85.7 | 85 | 85.6 | 90.6 | 88.9 | 92.4 | 94.9 | 93.2 | 87.6 | 88.8917 | 94.9 | 81.7
2026-05-08 | 18:45:00.000 | 88.9 | 88.3 | 87.5 | 89.1 | 89.8 | 88.2 | 85.6 | 103.1 | 102.3 | 102.4 | 104.2 | 97.7 | 93.925 | 104.2 | 85.6 | 88.4 | 93.2 | 92.8 | 87.1 | 89.3 | 96.4 | 93.4 | 96.3 | 95.5 | 90.3 | 90.6 | 92.8 | 92.175 | 96.4 | 87.1 | 104.5 | 111.6 | 106.2 | 105.8 | 104.9 | 106.7 | 108.6 | 101.6 | 108.6 | 112.7 | 106.4 | 93.6 | 105.9333 | 112.7 | 93.6
2026-05-08 | 19:00:00.000 | 67.1 | 66.8 | 66.1 | 67.2 | 67.4 | 64.6 | 62.9 | 78.2 | 76.5 | 74.4 | 74.4 | 68 | 69.4667 | 78.2 | 62.9 | 62.1 | 65.5 | 64.6 | 59.4 | 60.4 | 63.7 | 61.6 | 63.6 | 62.5 | 58.4 | 57.2 | 59.4 | 61.5333 | 65.5 | 57.2 | 79.8 | 80.3 | 74.5 | 74.2 | 72.7 | 74.3 | 77.7 | 75.4 | 79.6 | 82.9 | 77.2 | 70.9 | 76.625 | 82.9 | 70.9
2026-05-08 | 19:15:00.000 | 38.5 | 38 | 37.5 | 38.5 | 38.6 | 37 | 37.2 | 45.2 | 43.8 | 42.5 | 42.3 | 38.6 | 39.8083 | 45.2 | 37 | 35 | 37.2 | 36.4 | 32.8 | 33.4 | 34.9 | 33.7 | 34.7 | 33.9 | 31.2 | 30.2 | 31.5 | 33.7417 | 37.2 | 30.2 | 45.9 | 46.3 | 42.9 | 42.7 | 41.7 | 41.9 | 44.9 | 43.4 | 46.5 | 48.7 | 43.9 | 41.3 | 44.175 | 48.7 | 41.3
2026-05-08 | 19:30:00.000 | 17.3 | 17 | 16.9 | 17.8 | 17.6 | 16.8 | 17.2 | 21.3 | 20.6 | 20 | 19.8 | 17.9 | 18.35 | 21.3 | 16.8 | 16 | 17.4 | 16.6 | 14.6 | 14.9 | 16.4 | 15.8 | 16.3 | 16 | 14.7 | 14.6 | 15.2 | 15.7083 | 17.4 | 14.6 | 22.3 | 22.7 | 20.9 | 20.8 | 20.2 | 19.6 | 21.2 | 20.6 | 22.6 | 24.1 | 21 | 20 | 21.3333 | 24.1 | 19.6
2026-05-08 | 19:45:00.000 | 7.5 | 7.3 | 7.3 | 7.6 | 7.6 | 7.5 | 7.7 | 8.8 | 8.7 | 8.3 | 8.2 | 7.9 | 7.8667 | 8.8 | 7.3 | 7.5 | 7.8 | 7.6 | 7.2 | 7.6 | 8.2 | 8.6 | 9.1 | 9.5 | 9.9 | 10.2 | 10.7 | 8.6583 | 10.7 | 7.2 | 9.3 | 9.8 | 9.2 | 9.1 | 8.9 | 8.3 | 9 | 8.7 | 9.6 | 10.5 | 8.9 | 8.6 | 9.1583 | 10.5 | 8.3
2026-05-08 | 20:00:00.000 | 2.8 | 2.7 | 2.8 | 2.9 | 2.8 | 2.9 | 2.8 | 3 | 3 | 3 | 3 | 2.9 | 2.8833 | 3 | 2.7 | 2.6 | 2.8 | 2.8 | 2.6 | 2.6 | 2.9 | 2.9 | 3 | 3 | 2.8 | 3 | 3.1 | 2.8417 | 3.1 | 2.6 | 2.9 | 2.7 | 2.8 | 2.7 | 2.9 | 2.8 | 2.8 | 2.9 | 3 | 2.9 | 2.9 | 2.7 | 2.8333 | 3 | 2.7
2026-05-08 | 20:15:00.000 | 0.8 | 0.6 | 1.1 | 1.1 | 0.7 | 1 | 1.1 | 1.2 | 1.2 | 1.1 | 1 | 1 | 0.99167 | 1.2 | 0.6 | 1 | 1 | 0.7 | 1.1 | 1.1 | 1.2 | 1.2 | 0.7 | 1.3 | 1.1 | 1 | 0.9 | 1.025 | 1.3 | 0.7 | 1.1 | 1.1 | 1.2 | 1.1 | 1.2 | 1.1 | 1.1 | 1.2 | 1.1 | 1.2 | 1.2 | 1.1 | 1.1417 | 1.2 | 1.1
2026-05-08 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.3 | 0.175 | 0.7 | 0.1 | 0.1 | 0.2 | 0.9 | 0.1 | 0.7 | 0.2 | 0.2 | 0.7 | 0.2 | 0.1 | 0.1 | 0.8 | 0.35833 | 0.9 | 0.1 | 0.6 | 0.3 | 0.2 | 0.1 | 0.2 | 0.2 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.21667 | 0.6 | 0.1
2026-05-08 | 20:45:00.000 | 0.1 | 0 | 0.1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11818 | 0.3 | 0 | 0.1 | 0.1 | 0.5 | 0.1 | 0.4 | 0.1 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.4 | 0.20833 | 0.5 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.10833 | 0.2 | 0.1
2026-05-08 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.3 | 0 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-08 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320