## PR_Calc
PR CALCULATION
09 MAGGIO 2026 | [67 empty] | 9 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 50
RAW PR | [64 empty] | 0.87717 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 87.717
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 87.7577
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 87.7013
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-09 | 00:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8967.9
2026-05-09 | 00:15:00.000 | -2 | -0.0005 | -1.5 | -0.000375 | -0.0004375 | 0 | -0.0004375 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 00:30:00.000 | -1.9 | -0.000475 | -1.7 | -0.000425 | -0.00045 | 0 | -0.00045 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 00:45:00.000 | -2 | -0.0005 | -1.8 | -0.00045 | -0.000475 | 0 | -0.000475 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 01:00:00.000 | -2.1 | -0.000525 | -1.7 | -0.000425 | -0.000475 | 0 | -0.000475 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 01:15:00.000 | -2.5 | -0.000625 | -1.9 | -0.000475 | -0.00055 | 0 | -0.00055 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 01:30:00.000 | -1.6 | -0.0004 | -1.2 | -0.0003 | -0.00035 | 0 | -0.00035 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 01:45:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 02:00:00.000 | -1 | -0.00025 | -0.5 | -0.000125 | -0.0001875 | 0 | -0.0001875 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 02:15:00.000 | -1.4 | -0.00035 | -1.6 | -0.0004 | -0.000375 | 0 | -0.000375 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 02:30:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 02:45:00.000 | -1.3 | -0.000325 | -1 | -0.00025 | -0.0002875 | 0 | -0.0002875 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 03:00:00.000 | -1.7 | -0.000425 | -1.3 | -0.000325 | -0.000375 | 0 | -0.000375 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 03:15:00.000 | -1.1 | -0.000275 | 0 | 0 | -0.0001375 | 0 | -0.0001375 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 03:30:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 30657.6 | 30657.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 03:45:00.000 | -1 | -0.00025 | -0.6 | -0.00015 | -0.0002 | 0 | -0.0002 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 04:00:00.000 | -0.3 | -7.5e-05 | -0.1 | -2.5e-05 | -5e-05 | 0 | -5e-05 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 04:15:00.000 | -1 | -0.00025 | -0.3 | -7.5e-05 | -0.0001625 | 0 | -0.0001625 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 04:30:00.000 | -1 | -0.00025 | -0.6 | -0.00015 | -0.0002 | 0 | -0.0002 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 04:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 05:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 05:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 05:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 05:45:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 06:00:00.000 | 0.6 | 0.00015 | 0.8 | 0.0002 | 0.000175 | 0 | 0.000175 | 0.28571 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 06:15:00.000 | 6.6 | 0.00165 | 7.2 | 0.0018 | 0.001725 | 0 | 0.001725 | 0.086957 | 30657.6 | 30657.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 06:30:00.000 | 36.2 | 0.00905 | 37 | 0.00925 | 0.00915 | 0 | 0.00915 | 0.021858 | 30657.6 | 30657.7 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 06:45:00.000 | 88.3 | 0.022075 | 96.8 | 0.0242 | 0.023137 | 92.55 | 0.0242 | 0.091842 | 30657.7 | 30657.8 | 100 | 0.876 | 0 | 0 | 0 | 0 | 4.2955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35795 | 4.2955 | 0 | 4.2955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.175 | 0 | 0.43125 | 5.175 | 0 | 5.175 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1227 | 0 | 0 | 0 | 0 | 0 | 0.4657 | 5.1227 | 0 | 5.1227 | 1.0218
2026-05-09 | 07:00:00.000 | 134.2 | 0.03355 | 145.1 | 0.036275 | 0.034912 | 139.65 | 0.036275 | 0.078052 | 30657.8 | 30658 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 07:15:00.000 | 231.4 | 0.05785 | 240 | 0.06 | 0.058925 | 235.7 | 0.06 | 0.036487 | 30658 | 30658.5 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 07:30:00.000 | 245.8 | 0.06145 | 259.8 | 0.06495 | 0.0632 | 252.8 | 0.06495 | 0.05538 | 30658.5 | 30659.2 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 07:45:00.000 | 332.3 | 0.083075 | 341.6 | 0.0854 | 0.084237 | 336.95 | 0.0854 | 0.027601 | 30659.2 | 30660 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 08:00:00.000 | 355.4 | 0.08885 | 354.9 | 0.088725 | 0.088787 | 355.15 | 0.08885 | 0.0014079 | 30660 | 30661 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 08:15:00.000 | 440.5 | 0.11013 | 444.5 | 0.11113 | 0.11063 | 442.5 | 0.11113 | 0.0090395 | 30661 | 30662.1 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 08:30:00.000 | 711.6 | 0.1779 | 713.4 | 0.17835 | 0.17812 | 712.5 | 0.17835 | 0.0025263 | 30662.1 | 30663.8 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 08:45:00.000 | 790.5 | 0.19762 | 797.6 | 0.1994 | 0.19851 | 794.05 | 0.1994 | 0.0089415 | 30663.8 | 30665.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 09:00:00.000 | 866 | 0.2165 | 859.5 | 0.21488 | 0.21569 | 862.75 | 0.2165 | 0.007534 | 30665.9 | 30668.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 09:15:00.000 | 905.2 | 0.2263 | 896 | 0.224 | 0.22515 | 900.6 | 0.2263 | 0.010215 | 30668.2 | 30670.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 09:30:00.000 | 922.3 | 0.23058 | 913.1 | 0.22828 | 0.22942 | 917.7 | 0.23058 | 0.010025 | 30670.7 | 30673.2 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 09:45:00.000 | 939.7 | 0.23493 | 925.4 | 0.23135 | 0.23314 | 932.55 | 0.23493 | 0.015334 | 30673.2 | 30675.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 10:00:00.000 | 955 | 0.23875 | 936.8 | 0.2342 | 0.23647 | 945.9 | 0.23875 | 0.019241 | 30675.6 | 30678.1 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 10:15:00.000 | 944 | 0.236 | 924.7 | 0.23118 | 0.23359 | 934.35 | 0.236 | 0.020656 | 30678.1 | 30680.6 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 10:30:00.000 | 949.5 | 0.23738 | 927.1 | 0.23178 | 0.23458 | 938.3 | 0.23738 | 0.023873 | 30680.6 | 30683.1 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 10:45:00.000 | 982.2 | 0.24555 | 957.9 | 0.23947 | 0.24251 | 970.05 | 0.24555 | 0.02505 | 30683.1 | 30685.5 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 11:00:00.000 | 930.1 | 0.23253 | 901.6 | 0.2254 | 0.22896 | 915.85 | 0.23253 | 0.031119 | 30685.5 | 30688 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 11:15:00.000 | 982.4 | 0.2456 | 950.3 | 0.23757 | 0.24159 | 966.35 | 0.2456 | 0.033218 | 30688 | 30690.5 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 11:30:00.000 | 987.3 | 0.24682 | 956.6 | 0.23915 | 0.24299 | 971.95 | 0.24682 | 0.031586 | 30690.5 | 30693 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 11:45:00.000 | 980.5 | 0.24513 | 948.8 | 0.2372 | 0.24116 | 964.65 | 0.24513 | 0.032862 | 30693 | 30695.4 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 12:00:00.000 | 972.6 | 0.24315 | 969.6 | 0.2424 | 0.24278 | 971.1 | 0.24315 | 0.0030893 | 30695.4 | 30697.9 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 12:15:00.000 | 992.4 | 0.2481 | 954.1 | 0.23853 | 0.24331 | 973.25 | 0.2481 | 0.039353 | 30697.9 | 30700.3 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 12:30:00.000 | 960.1 | 0.24003 | 923.7 | 0.23093 | 0.23548 | 941.9 | 0.24003 | 0.038645 | 30700.3 | 30702.8 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 12:45:00.000 | 939.5 | 0.23488 | 899 | 0.22475 | 0.22981 | 919.25 | 0.23488 | 0.044058 | 30702.8 | 30705.2 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 13:00:00.000 | 915.2 | 0.2288 | 881.3 | 0.22032 | 0.22456 | 898.25 | 0.2288 | 0.03774 | 30705.2 | 30707.7 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 13:15:00.000 | 935.7 | 0.23393 | 903.3 | 0.22582 | 0.22987 | 919.5 | 0.23393 | 0.035237 | 30707.7 | 30710.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 13:30:00.000 | 904.1 | 0.22603 | 875.5 | 0.21887 | 0.22245 | 889.8 | 0.22603 | 0.032142 | 30710.1 | 30712.6 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 13:45:00.000 | 766.4 | 0.1916 | 741.1 | 0.18527 | 0.18844 | 753.75 | 0.1916 | 0.033566 | 30712.6 | 30714.9 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 14:00:00.000 | 632.5 | 0.15812 | 617.6 | 0.1544 | 0.15626 | 625.05 | 0.15812 | 0.023838 | 30714.9 | 30716.9 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 14:15:00.000 | 678.8 | 0.1697 | 654.2 | 0.16355 | 0.16662 | 666.5 | 0.1697 | 0.036909 | 30716.9 | 30718.7 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 14:30:00.000 | 702.1 | 0.17553 | 688.9 | 0.17222 | 0.17388 | 695.5 | 0.17553 | 0.018979 | 30718.7 | 30720.5 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 14:45:00.000 | 835.6 | 0.2089 | 810.6 | 0.20265 | 0.20577 | 823.1 | 0.2089 | 0.030373 | 30720.5 | 30722.7 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 15:00:00.000 | 879.7 | 0.21993 | 859.5 | 0.21488 | 0.2174 | 869.6 | 0.21993 | 0.023229 | 30722.7 | 30725 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 15:15:00.000 | 736.1 | 0.18402 | 722.7 | 0.18068 | 0.18235 | 729.4 | 0.18402 | 0.018371 | 30725 | 30727.3 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 15:30:00.000 | 333 | 0.08325 | 331.2 | 0.0828 | 0.083025 | 332.1 | 0.08325 | 0.0054201 | 30727.3 | 30728.7 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 15:45:00.000 | 199.8 | 0.04995 | 188.8 | 0.0472 | 0.048575 | 194.3 | 0.04995 | 0.056613 | 30728.7 | 30729.4 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 16:00:00.000 | 377.1 | 0.094275 | 361.8 | 0.09045 | 0.092363 | 369.45 | 0.094275 | 0.041413 | 30729.4 | 30730.2 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 16:15:00.000 | 582.9 | 0.14572 | 565.4 | 0.14135 | 0.14354 | 574.15 | 0.14572 | 0.03048 | 30730.2 | 30731.6 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 16:30:00.000 | 462.9 | 0.11572 | 454.8 | 0.1137 | 0.11471 | 458.85 | 0.11572 | 0.017653 | 30731.6 | 30733.2 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 16:45:00.000 | 288.7 | 0.072175 | 271.7 | 0.067925 | 0.07005 | 280.2 | 0.072175 | 0.060671 | 30733.2 | 30734.3 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 17:00:00.000 | 117.7 | 0.029425 | 107.7 | 0.026925 | 0.028175 | 112.7 | 0.029425 | 0.088731 | 30734.3 | 30734.9 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 17:15:00.000 | 94.9 | 0.023725 | 82.9 | 0.020725 | 0.022225 | 88.9 | 0.023725 | 0.13498 | 30734.9 | 30735.1 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 17:30:00.000 | 171.3 | 0.042825 | 159 | 0.03975 | 0.041288 | 165.15 | 0.042825 | 0.074478 | 30735.1 | 30735.6 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 17:45:00.000 | 114.8 | 0.0287 | 108.6 | 0.02715 | 0.027925 | 111.7 | 0.0287 | 0.055506 | 30735.6 | 30736 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 18:00:00.000 | 44.2 | 0.01105 | 41.3 | 0.010325 | 0.010687 | 0 | 0.010687 | 0.067836 | 30736 | 30736.2 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 18:15:00.000 | 89.4 | 0.02235 | 90.6 | 0.02265 | 0.0225 | 90 | 0.02265 | 0.013333 | 30736.2 | 30736.4 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 18:30:00.000 | 112.3 | 0.028075 | 110.2 | 0.02755 | 0.027813 | 111.25 | 0.028075 | 0.018876 | 30736.4 | 30736.8 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 18:45:00.000 | 91 | 0.02275 | 89.5 | 0.022375 | 0.022562 | 90.25 | 0.02275 | 0.01662 | 30736.8 | 30737.1 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 19:00:00.000 | 59 | 0.01475 | 58.2 | 0.01455 | 0.01465 | 58.6 | 0.01475 | 0.013652 | 30737.1 | 30737.3 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 19:15:00.000 | 50.7 | 0.012675 | 51.8 | 0.01295 | 0.012813 | 51.25 | 0.01295 | 0.021463 | 30737.3 | 30737.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 19:30:00.000 | 33.1 | 0.008275 | 34.8 | 0.0087 | 0.0084875 | 0 | 0.0084875 | 0.050074 | 30737.4 | 30737.6 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 19:45:00.000 | 21.5 | 0.005375 | 22.7 | 0.005675 | 0.005525 | 0 | 0.005525 | 0.054299 | 30737.6 | 30737.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 20:00:00.000 | 10.6 | 0.00265 | 10.8 | 0.0027 | 0.002675 | 0 | 0.002675 | 0.018692 | 30737.6 | 30737.7 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 20:15:00.000 | 0.9 | 0.000225 | 1.1 | 0.000275 | 0.00025 | 0 | 0.00025 | 0.2 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 20:30:00.000 | -0.7 | -0.000175 | -0.4 | -0.0001 | -0.0001375 | 0 | -0.0001375 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 20:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 21:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 21:15:00.000 | -1 | -0.00025 | -0.9 | -0.000225 | -0.0002375 | 0 | -0.0002375 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 21:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 21:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 22:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 22:15:00.000 | -1 | -0.00025 | -0.3 | -7.5e-05 | -0.0001625 | 0 | -0.0001625 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 22:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 22:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 23:00:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 23:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 23:30:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
2026-05-09 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218
PR for each inverter |  |  | 7.445 |  | 7.287 | 7.366 |  | 7.4633 |  |  |  | 80100 |  | 0.88894 | 0.88095 | 0.88685 | 0.88986 | 0.88812 | 0.88608 | 0.89001 | 0.87146 | 0.86683 | 0.86593 | 0.86406 | 0.89513 | #DIV/0! | #DIV/0! | #DIV/0! | 4.2955 | 0.89869 | 0.88272 | 0.88286 | 0.90526 | 0.9103 | 0.86717 | 0.88633 | 0.86476 | 0.85911 | 0.88442 | 0.86234 | 0.867 |  |  |  | 5.175 | 0.87173 | 0.86639 | 0.86625 | 0.8707 | 0.86849 | 0.87226 | 0.87087 | 0.8634 | 0.86197 | 0.85871 | 0.87211 | 0.9047 | #DIV/0! | #DIV/0! | #DIV/0! | 5.1227 |  | 0.87758 |  | #DIV/0! | #DIV/0! | 9.1483e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-09 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 06:30:00.000 | 6.2 | 6.2 | 6.3 | 6.1 | 5.8 | 6.3 | 6.3 | 6.4 | 6.5 | 6.2 | 6.6 | 6.5 | 6.2833 | 6.6 | 5.8 | 6 | 6.1 | 7.3 | 6.3 | 5.1 | 6.5 | 6.2 | 7.8 | 6.5 | 6.2 | 6.5 | 7.2 | 6.475 | 7.8 | 5.1 | 7 | 6.1 | 6.6 | 6.6 | 6.2 | 6.6 | 6.4 | 6.5 | 6.5 | 6.1 | 6.7 | 5.6 | 6.4083 | 7 | 5.6
2026-05-09 | 06:45:00.000 | 7.5 | 6.1 | 7.7 | 20.9 | 0 | 20 | 20.5 | 20.2 | 21.3 | 21.4 | 21.7 | 21.7 | 17.1818 | 21.7 | 0 | 19.7 | 19.5 | 20.5 | 20.4 | 11.2 | 21.6 | 21.6 | 22.3 | 22.8 | 21.2 | 0 | 22.5 | 20.3 | 22.8 | 0 | 21.5 | 18.2 | 19.9 | 21 | 20.8 | 22.4 | 0 | 20.7 | 19.7 | 18.8 | 21.7 | 20.7 | 20.4909 | 22.4 | 0
2026-05-09 | 07:00:00.000 | 34.5 | 34 | 35.7 | 35.7 | 15.1 | 34.6 | 34 | 34.6 | 35.7 | 36.2 | 37 | 36.1 | 33.6 | 37 | 15.1 | 32.8 | 32.1 | 33.6 | 34.6 | 34.1 | 35.9 | 35.9 | 37 | 38.1 | 35.7 | 24.3 | 37.6 | 34.3083 | 38.1 | 24.3 | 38 | 34 | 35.5 | 37.5 | 37.5 | 39.7 | 9 | 37.6 | 36.3 | 33.9 | 37.5 | 36.2 | 34.3917 | 39.7 | 9
2026-05-09 | 07:15:00.000 | 67.1 | 66.5 | 68.9 | 68.4 | 68.6 | 66.9 | 66.3 | 69.2 | 69.8 | 69.7 | 71.3 | 69.8 | 68.5417 | 71.3 | 66.3 | 63.9 | 63.7 | 65.4 | 66.1 | 65.6 | 70 | 68.8 | 71.1 | 72.7 | 68.7 | 72.6 | 71.8 | 68.3667 | 72.7 | 63.7 | 72.5 | 67.7 | 70.4 | 73.2 | 72.3 | 75 | 73.3 | 72 | 70.7 | 68 | 72.9 | 67.9 | 71.325 | 75 | 67.7
2026-05-09 | 07:30:00.000 | 76.6 | 75.9 | 77.6 | 77.4 | 77.3 | 76 | 75.4 | 79.3 | 79 | 78.6 | 79.8 | 78.3 | 77.6 | 79.8 | 75.4 | 72.4 | 73.2 | 74.2 | 74.2 | 73.9 | 79.1 | 77.2 | 79.5 | 80.6 | 76.6 | 80.8 | 79.9 | 76.8 | 80.8 | 72.4 | 81.6 | 78.2 | 80.5 | 82.8 | 78.7 | 83.9 | 83 | 81.4 | 80.4 | 72.7 | 83 | 76.7 | 80.2417 | 83.9 | 72.7
2026-05-09 | 07:45:00.000 | 104.4 | 103.6 | 105.7 | 105.7 | 105.8 | 104.6 | 104 | 109.4 | 108.4 | 108 | 109.4 | 106.9 | 106.325 | 109.4 | 103.6 | 100 | 102.3 | 103 | 101.9 | 102 | 109.4 | 105.9 | 108.9 | 110 | 104.9 | 110 | 108.9 | 105.6 | 110 | 100 | 110.3 | 107 | 109.3 | 111.9 | 110.6 | 112 | 111.7 | 109.7 | 108.8 | 107.1 | 112.8 | 102.2 | 109.45 | 112.8 | 102.2
2026-05-09 | 08:00:00.000 | 111.6 | 110.7 | 112.5 | 112.9 | 112.7 | 111.3 | 111.3 | 117.4 | 115.9 | 115.3 | 116.5 | 113.6 | 113.475 | 117.4 | 110.7 | 106.7 | 109.6 | 110.1 | 107.9 | 108.2 | 116.5 | 112.3 | 115.7 | 116 | 110.7 | 115.5 | 114.6 | 111.9833 | 116.5 | 106.7 | 117.4 | 115.2 | 116.4 | 119.2 | 118.8 | 119.7 | 119.6 | 112.5 | 116.4 | 114.5 | 119.7 | 109.2 | 116.55 | 119.7 | 109.2
2026-05-09 | 08:15:00.000 | 136.9 | 136 | 133.5 | 139 | 138.5 | 137.7 | 138.4 | 145.8 | 143.8 | 141.8 | 144.2 | 140.4 | 139.6667 | 145.8 | 133.5 | 132.3 | 135.9 | 137 | 133.3 | 133.5 | 144.7 | 139 | 143.5 | 144 | 137.2 | 142.8 | 140.8 | 138.6667 | 144.7 | 132.3 | 142.3 | 141 | 142.9 | 146.1 | 144.5 | 145.3 | 145.5 | 141.2 | 141.3 | 140.4 | 145.9 | 131.4 | 142.3167 | 146.1 | 131.4
2026-05-09 | 08:30:00.000 | 223.1 | 220.7 | 223.4 | 224.6 | 224.1 | 223.2 | 223.5 | 236.1 | 232.5 | 231.5 | 232.6 | 226.1 | 226.7833 | 236.1 | 220.7 | 213.5 | 220.8 | 220.9 | 214.8 | 215.5 | 234.7 | 223.7 | 231 | 222.7 | 220.5 | 230 | 226.7 | 222.9 | 234.7 | 213.5 | 232.1 | 230.8 | 232.9 | 236.9 | 235.8 | 237 | 238.6 | 232.4 | 232.4 | 230.3 | 236.9 | 215.5 | 232.6333 | 238.6 | 215.5
2026-05-09 | 08:45:00.000 | 246.7 | 244.2 | 247 | 248.6 | 247.8 | 246.9 | 248.5 | 261.5 | 257.8 | 256.2 | 256.8 | 250.6 | 251.05 | 261.5 | 244.2 | 236.3 | 245.4 | 244.7 | 237.4 | 238.6 | 259.2 | 247 | 255.7 | 246.6 | 244 | 254.7 | 250.6 | 246.6833 | 259.2 | 236.3 | 257.1 | 257 | 258.8 | 263.1 | 252.5 | 261.8 | 263.8 | 247.3 | 257.1 | 256.6 | 261.5 | 238.5 | 256.2583 | 263.8 | 238.5
2026-05-09 | 09:00:00.000 | 258 | 264.9 | 268.4 | 270 | 268.2 | 269.2 | 270.9 | 280.6 | 278.2 | 276.6 | 277.4 | 272.4 | 271.2333 | 280.6 | 258 | 248.4 | 269 | 266.1 | 257.4 | 259.1 | 278.6 | 267.9 | 276.1 | 275 | 264.3 | 255.3 | 271 | 265.6833 | 278.6 | 248.4 | 275.7 | 258.1 | 277.4 | 279.1 | 279.1 | 278.4 | 279.9 | 274.8 | 275.7 | 276.9 | 279.8 | 256.5 | 274.2833 | 279.9 | 256.5
2026-05-09 | 09:15:00.000 | 278.5 | 275.9 | 277.8 | 279.6 | 278.7 | 278.5 | 280.9 | 281.6 | 280.8 | 281.6 | 281.2 | 280.9 | 279.6667 | 281.6 | 275.9 | 267.2 | 278.7 | 276.5 | 266.7 | 268.5 | 281.3 | 277.3 | 281.3 | 281.3 | 275.3 | 280.8 | 281.7 | 276.3833 | 281.7 | 266.7 | 281.6 | 282 | 281.5 | 281.6 | 281.6 | 281.2 | 281.5 | 281.5 | 281.5 | 281.2 | 281.2 | 257.4 | 279.4833 | 282 | 257.4
2026-05-09 | 09:30:00.000 | 280.6 | 279.7 | 280.3 | 280.7 | 280.5 | 280.8 | 281.5 | 281.5 | 280.6 | 281.5 | 281.3 | 280.7 | 280.8083 | 281.5 | 279.7 | 270.1 | 279.8 | 279.9 | 270.1 | 271.7 | 281.1 | 280.3 | 281.3 | 281.3 | 279.5 | 281.3 | 271 | 277.2833 | 281.3 | 270.1 | 281.7 | 281.8 | 281.5 | 281.4 | 281.4 | 281.1 | 281.3 | 281.6 | 281.4 | 281.2 | 281 | 272.9 | 280.6917 | 281.8 | 272.9
2026-05-09 | 09:45:00.000 | 281 | 281.1 | 281.2 | 281.4 | 281.2 | 281.6 | 281.5 | 271.9 | 280.8 | 281 | 281.3 | 281 | 280.4167 | 281.6 | 271.9 | 275.9 | 281.6 | 281.6 | 276.6 | 278.3 | 281.3 | 281.1 | 281.2 | 281.1 | 281.2 | 281.3 | 281.6 | 280.2333 | 281.6 | 275.9 | 281.6 | 281.8 | 281.6 | 271.3 | 281.6 | 281.2 | 281.5 | 281.5 | 281.3 | 281.2 | 281 | 277.9 | 280.2917 | 281.8 | 271.3
2026-05-09 | 10:00:00.000 | 279.7 | 279.3 | 280.5 | 279.7 | 280.7 | 280.8 | 280 | 281.5 | 280.2 | 280.8 | 281 | 280 | 280.35 | 281.5 | 279.3 | 278 | 280.2 | 279.4 | 279 | 279.1 | 280.5 | 280.2 | 280.1 | 280.6 | 280.5 | 280.9 | 281.3 | 279.9833 | 281.3 | 278 | 280.6 | 280.9 | 280.7 | 280.3 | 280 | 279.6 | 280.9 | 280.5 | 280.7 | 280.7 | 280.6 | 279.3 | 280.4 | 280.9 | 279.3
2026-05-09 | 10:15:00.000 | 281.2 | 280.6 | 280.8 | 281.1 | 281.3 | 281.5 | 280.7 | 281.7 | 281.1 | 281.3 | 281.4 | 281.3 | 281.1667 | 281.7 | 280.6 | 273.8 | 280.9 | 280.3 | 275.7 | 277.6 | 281.4 | 281.2 | 281.2 | 281.5 | 281.4 | 281.1 | 281.4 | 279.7917 | 281.5 | 273.8 | 281.5 | 281.6 | 281.2 | 281.6 | 281.2 | 280.9 | 281.4 | 281.5 | 281.3 | 281.2 | 281 | 276.2 | 280.8833 | 281.6 | 276.2
2026-05-09 | 10:30:00.000 | 281 | 280.3 | 270.8 | 281.2 | 280.3 | 281 | 281.1 | 281.7 | 281.2 | 281.2 | 281.3 | 280.9 | 280.1667 | 281.7 | 270.8 | 273.9 | 280.4 | 280.3 | 275.4 | 277.1 | 281.4 | 280.4 | 281.1 | 281.4 | 280.2 | 281.1 | 281.4 | 279.5083 | 281.4 | 273.9 | 281.5 | 281.6 | 281.2 | 281.6 | 281.3 | 281.1 | 281.4 | 281.1 | 271.6 | 281.3 | 281 | 276.8 | 280.125 | 281.6 | 271.6
2026-05-09 | 10:45:00.000 | 281 | 281 | 281.1 | 281.6 | 281.2 | 280.7 | 281.4 | 281.7 | 281.1 | 281.3 | 281.3 | 271.4 | 280.4 | 281.7 | 271.4 | 279.2 | 281.6 | 281 | 280.1 | 280.1 | 281.4 | 281.2 | 281.2 | 281.6 | 281.4 | 281.1 | 281.4 | 280.9417 | 281.6 | 279.2 | 281.5 | 281.6 | 281.1 | 271.9 | 281.2 | 281 | 281.4 | 281.5 | 281.4 | 281.8 | 281 | 280.4 | 280.4833 | 281.8 | 271.9
2026-05-09 | 11:00:00.000 | 279 | 277.3 | 278.4 | 279.3 | 279.3 | 278.6 | 280 | 281.6 | 281.2 | 281.2 | 281.2 | 279.6 | 279.725 | 281.6 | 277.3 | 267.3 | 278.7 | 276.9 | 269.7 | 272 | 281.4 | 277 | 270.9 | 280.7 | 275.7 | 280.9 | 281.4 | 276.05 | 281.4 | 267.3 | 281.5 | 281.4 | 280.7 | 281.7 | 281.3 | 281.3 | 281.6 | 280.8 | 281.6 | 280.9 | 281.1 | 260.6 | 279.5417 | 281.7 | 260.6
2026-05-09 | 11:15:00.000 | 280.9 | 280.3 | 281.1 | 281.2 | 280.8 | 280.7 | 281.1 | 281.2 | 281 | 281.6 | 281.7 | 281.6 | 281.1 | 281.7 | 280.3 | 278.5 | 280.8 | 280.8 | 279.1 | 280.1 | 281.3 | 280.5 | 281 | 280.6 | 280.9 | 281.3 | 281.6 | 280.5417 | 281.6 | 278.5 | 281.4 | 281 | 280.4 | 281.8 | 281.3 | 281.1 | 281.7 | 281.6 | 281.2 | 281.1 | 281.1 | 279.8 | 281.125 | 281.8 | 279.8
2026-05-09 | 11:30:00.000 | 281 | 280.8 | 280.2 | 260.9 | 280.3 | 281 | 281.2 | 281.2 | 280.9 | 281 | 281.1 | 280.9 | 279.2083 | 281.2 | 260.9 | 278.1 | 280.3 | 280.3 | 277.8 | 277.9 | 281.4 | 270.8 | 281.1 | 271.6 | 280 | 281.1 | 281.2 | 278.4667 | 281.4 | 270.8 | 281.4 | 281 | 280.8 | 281.7 | 281.4 | 281.5 | 281.6 | 281.5 | 281.1 | 281.3 | 281.1 | 279.5 | 281.1583 | 281.7 | 279.5
2026-05-09 | 11:45:00.000 | 277.6 | 277 | 278.2 | 279.6 | 278.7 | 272.8 | 280.9 | 281 | 280.3 | 281 | 280 | 276.5 | 278.6333 | 281 | 272.8 | 271.4 | 276.4 | 277.9 | 274.6 | 271.9 | 279.7 | 276.9 | 279.3 | 278.3 | 276.6 | 279.8 | 280.7 | 276.9583 | 280.7 | 271.4 | 280.3 | 278.6 | 279.8 | 278.3 | 278.6 | 277.8 | 280.2 | 279.3 | 279 | 278.5 | 280.2 | 270.1 | 278.3917 | 280.3 | 270.1
2026-05-09 | 12:00:00.000 | 269.7 | 260.2 | 269.1 | 268.9 | 270 | 265.4 | 270.3 | 273.9 | 275.5 | 272.7 | 272.2 | 275 | 270.2417 | 275.5 | 260.2 | 264.4 | 272.3 | 269.6 | 269.6 | 269.2 | 269.8 | 272.1 | 273.3 | 264.1 | 271.5 | 265.4 | 274.6 | 269.6583 | 274.6 | 264.1 | 276.5 | 278.1 | 279.1 | 277.6 | 277.4 | 277.2 | 277.3 | 274.7 | 273.8 | 277.3 | 272.9 | 267 | 275.7417 | 279.1 | 267
2026-05-09 | 12:15:00.000 | 280.5 | 279.9 | 279.7 | 280.6 | 271.6 | 279.9 | 280.1 | 281.4 | 280.1 | 281.4 | 281.2 | 279.8 | 279.6833 | 281.4 | 271.6 | 265.2 | 280.4 | 279.1 | 276.6 | 277.8 | 278.2 | 278.7 | 280.5 | 280.9 | 278.9 | 280.6 | 281.1 | 278.1667 | 281.1 | 265.2 | 280.1 | 280.9 | 280.6 | 281.2 | 281 | 281.4 | 280.9 | 280.7 | 279.9 | 271.3 | 280.7 | 277.3 | 279.6667 | 281.4 | 271.3
2026-05-09 | 12:30:00.000 | 279.9 | 279.5 | 280.3 | 280.3 | 280.5 | 279.9 | 280.4 | 281 | 281.6 | 280.7 | 280.4 | 279.7 | 280.35 | 281.6 | 279.5 | 275.6 | 269.6 | 280 | 275.9 | 276.7 | 280.5 | 278.8 | 280.2 | 279.7 | 278.4 | 280.5 | 280.5 | 278.0333 | 280.5 | 269.6 | 280.7 | 280.8 | 280.7 | 281.2 | 281 | 281.2 | 281.3 | 280.6 | 280.9 | 281.1 | 280.6 | 277.2 | 280.6083 | 281.3 | 277.2
2026-05-09 | 12:45:00.000 | 275.7 | 273.9 | 273.9 | 276.2 | 276.1 | 274.5 | 277.2 | 280 | 279.3 | 276.6 | 276.6 | 275.5 | 276.2917 | 280 | 273.9 | 269.5 | 266.3 | 275.1 | 269.8 | 270.3 | 276.9 | 272 | 276.9 | 276.7 | 272.6 | 276 | 275.4 | 273.125 | 276.9 | 266.3 | 278.2 | 278.3 | 276.7 | 269.2 | 277.8 | 277.5 | 279.2 | 276.2 | 276 | 276.2 | 278.9 | 268.6 | 276.0667 | 279.2 | 268.6
2026-05-09 | 13:00:00.000 | 275.3 | 273.5 | 275.9 | 276.1 | 276.1 | 275.5 | 276.6 | 281.1 | 280.8 | 279.1 | 279 | 276.6 | 277.1333 | 281.1 | 273.5 | 263.6 | 274.6 | 274 | 263.4 | 265.6 | 279.6 | 273.2 | 278.9 | 279.3 | 271.6 | 278.6 | 279.3 | 273.475 | 279.6 | 263.4 | 280.9 | 280.2 | 280.8 | 280.7 | 280.4 | 279.8 | 280.4 | 280.1 | 265.2 | 279.8 | 269.9 | 264.5 | 276.8917 | 280.9 | 264.5
2026-05-09 | 13:15:00.000 | 279.9 | 278.9 | 279.9 | 280 | 280.9 | 279.4 | 280.3 | 281.4 | 281.5 | 281.2 | 281.1 | 280.9 | 280.45 | 281.5 | 278.9 | 269.3 | 279.5 | 278.4 | 270.6 | 272.5 | 280.8 | 278.3 | 281.1 | 281.2 | 277.5 | 281.4 | 281.5 | 277.675 | 281.5 | 269.3 | 281.7 | 281.5 | 281.9 | 281.8 | 281.7 | 281 | 281.9 | 281 | 277 | 272 | 281.3 | 272 | 279.5667 | 281.9 | 272
2026-05-09 | 13:30:00.000 | 274.7 | 272.4 | 273.6 | 274.7 | 274.2 | 273 | 274.5 | 280.2 | 279 | 277.9 | 277.4 | 275.2 | 275.5667 | 280.2 | 272.4 | 262.6 | 273.4 | 271.8 | 263.6 | 265.3 | 278.5 | 271.9 | 277.3 | 276.7 | 270.9 | 276.8 | 277.5 | 272.1917 | 278.5 | 262.6 | 279.6 | 279.3 | 280.2 | 280 | 279.3 | 278.9 | 280.3 | 277.7 | 278.4 | 278.7 | 279.5 | 266.1 | 278.1667 | 280.3 | 266.1
2026-05-09 | 13:45:00.000 | 238.3 | 235.9 | 239.2 | 239.4 | 232.1 | 229.7 | 239.6 | 255.4 | 248.9 | 246.5 | 245.8 | 238.5 | 240.775 | 255.4 | 229.7 | 229.8 | 239.5 | 238.1 | 228.6 | 231 | 237.8 | 234.7 | 241 | 233.8 | 225.7 | 244.3 | 245.4 | 235.8083 | 245.4 | 225.7 | 250.5 | 248.4 | 248 | 249.8 | 248.4 | 246.6 | 250.3 | 245.1 | 246 | 245.6 | 248.5 | 229.4 | 246.3833 | 250.5 | 229.4
2026-05-09 | 14:00:00.000 | 202.5 | 199.6 | 199.5 | 200.9 | 199.5 | 196.8 | 192.6 | 210.8 | 210.2 | 208 | 204.9 | 202.6 | 202.325 | 210.8 | 192.6 | 188.7 | 198.2 | 195.5 | 189.5 | 191.1 | 206.8 | 194 | 205.6 | 199.2 | 198.6 | 208.3 | 209.9 | 198.7833 | 209.9 | 188.7 | 209.7 | 210.1 | 213 | 210.7 | 208.8 | 210.3 | 202.7 | 199.5 | 209.7 | 210.2 | 207.9 | 193.5 | 207.175 | 213 | 193.5
2026-05-09 | 14:15:00.000 | 211.7 | 210 | 213.4 | 211.5 | 215.4 | 205.9 | 212.5 | 217.2 | 215.4 | 223.6 | 214.5 | 212.6 | 213.6417 | 223.6 | 205.9 | 204.3 | 207.6 | 208.1 | 207.3 | 211.1 | 222.9 | 211 | 216.7 | 214.3 | 207 | 215.4 | 217.7 | 211.95 | 222.9 | 204.3 | 222.1 | 219.4 | 209.4 | 219.1 | 219.3 | 222.3 | 218.9 | 216.3 | 215.8 | 215.3 | 219 | 205.8 | 216.8917 | 222.3 | 205.8
2026-05-09 | 14:30:00.000 | 219.4 | 215.5 | 210.2 | 218.4 | 218.1 | 221.2 | 220.7 | 230.9 | 221.1 | 223.4 | 218.2 | 214.6 | 219.3083 | 230.9 | 210.2 | 207.3 | 216.2 | 212.4 | 201.8 | 210.9 | 220.1 | 216.8 | 223.4 | 223.3 | 216.3 | 223.6 | 223.7 | 216.3167 | 223.7 | 201.8 | 229.9 | 230.8 | 216.1 | 230.4 | 215.7 | 230.8 | 223.6 | 219.4 | 220.8 | 212.4 | 225 | 210 | 222.075 | 230.8 | 210
2026-05-09 | 14:45:00.000 | 253 | 240.9 | 255.6 | 250.8 | 255.7 | 252.8 | 250.7 | 260.6 | 257.2 | 263.9 | 258.5 | 257.6 | 254.775 | 263.9 | 240.9 | 239.5 | 249.6 | 252.3 | 239.6 | 241.9 | 261.8 | 250.1 | 263.5 | 260.5 | 252.4 | 258.1 | 259.6 | 252.4083 | 263.5 | 239.5 | 258 | 265.7 | 260.4 | 265.4 | 262.4 | 263.9 | 265.3 | 263.5 | 254.2 | 243.4 | 263.2 | 237.4 | 258.5667 | 265.7 | 237.4
2026-05-09 | 15:00:00.000 | 264.8 | 254.9 | 262.9 | 263.7 | 263.6 | 262.4 | 263.1 | 273 | 271.8 | 270 | 269.4 | 266.1 | 265.475 | 273 | 254.9 | 246.1 | 262.5 | 260.4 | 254.6 | 256.5 | 271.3 | 263.2 | 270 | 270.1 | 263.2 | 269.9 | 271.6 | 263.2833 | 271.6 | 246.1 | 266.1 | 273.3 | 272.3 | 273.2 | 272.8 | 272.4 | 274.4 | 271 | 272.3 | 271.9 | 273.6 | 248.1 | 270.1167 | 274.4 | 248.1
2026-05-09 | 15:15:00.000 | 220.4 | 219.2 | 222.1 | 221.5 | 222.3 | 220.3 | 221 | 224.7 | 226.4 | 222.6 | 220.9 | 220.8 | 221.85 | 226.4 | 219.2 | 214.1 | 212.4 | 216.9 | 212.4 | 213.7 | 225.7 | 219.6 | 222.7 | 213.1 | 219.8 | 225 | 225.8 | 218.4333 | 225.8 | 212.4 | 229.8 | 231.3 | 227.6 | 228.6 | 229.8 | 229.9 | 231.4 | 226.2 | 225.6 | 224.8 | 230.6 | 215.1 | 227.5583 | 231.4 | 215.1
2026-05-09 | 15:30:00.000 | 110.5 | 108.9 | 108.2 | 110 | 108.4 | 107.7 | 109.1 | 115.5 | 115.2 | 113.4 | 112.9 | 112.7 | 111.0417 | 115.5 | 107.7 | 103.3 | 107.3 | 106.4 | 104.7 | 105.3 | 115.9 | 107.3 | 114.9 | 114.5 | 110.4 | 110.1 | 117.1 | 109.7667 | 117.1 | 103.3 | 120.1 | 117.9 | 118.1 | 119.7 | 119 | 119.9 | 118.7 | 115.1 | 114.8 | 114.8 | 118.8 | 105.3 | 116.85 | 120.1 | 105.3
2026-05-09 | 15:45:00.000 | 67 | 65.8 | 66.1 | 66.2 | 66.3 | 65.6 | 66 | 69.7 | 68.9 | 68 | 67.8 | 67.4 | 67.0667 | 69.7 | 65.6 | 63 | 65.1 | 64.7 | 63.6 | 65 | 65.5 | 65.3 | 67.7 | 67.9 | 65.6 | 69.3 | 69.7 | 66.0333 | 69.7 | 63 | 70.6 | 68.8 | 68.5 | 69 | 68.1 | 68.8 | 69.8 | 67.9 | 67.9 | 67.6 | 70.2 | 63.7 | 68.4083 | 70.6 | 63.7
2026-05-09 | 16:00:00.000 | 119.9 | 118.1 | 118.7 | 119.2 | 119.2 | 117.9 | 118.9 | 125.6 | 124.4 | 123.1 | 122.5 | 121.7 | 120.7667 | 125.6 | 117.9 | 113.4 | 117.4 | 116.7 | 114.4 | 116.8 | 123.8 | 118.1 | 122.8 | 123.3 | 119.3 | 120.1 | 126.6 | 119.3917 | 126.6 | 113.4 | 126.7 | 123.8 | 122.9 | 123.7 | 122.7 | 123.5 | 125.4 | 122.1 | 122.3 | 121.7 | 126.2 | 111.1 | 122.675 | 126.7 | 111.1
2026-05-09 | 16:15:00.000 | 181.8 | 179.2 | 180.6 | 180.6 | 180.9 | 179.3 | 180.5 | 191.5 | 185.4 | 186.9 | 186.8 | 184.3 | 183.15 | 191.5 | 179.2 | 172.4 | 179 | 177.6 | 173.2 | 177.1 | 189 | 179.1 | 187.1 | 181.7 | 174.1 | 190.3 | 192 | 181.05 | 192 | 172.4 | 192.6 | 183 | 187.9 | 189.5 | 187.6 | 181.2 | 191.8 | 186.3 | 186.6 | 186.2 | 191.7 | 173.8 | 186.5167 | 192.6 | 173.8
2026-05-09 | 16:30:00.000 | 148.3 | 145.8 | 145 | 146.6 | 145.2 | 143.9 | 145.6 | 154.6 | 149.2 | 151.7 | 150.4 | 150.2 | 148.0417 | 154.6 | 143.9 | 138.1 | 143.9 | 141.8 | 139.8 | 142.5 | 154.1 | 146.2 | 151.6 | 149.9 | 146.7 | 155 | 151.8 | 146.7833 | 155 | 138.1 | 158.7 | 155.4 | 147.7 | 156.4 | 154.9 | 156.4 | 152.2 | 153.8 | 153.9 | 152.7 | 157 | 142.6 | 153.475 | 158.7 | 142.6
2026-05-09 | 16:45:00.000 | 95.9 | 94.3 | 94.4 | 92.3 | 95.3 | 93.9 | 95.3 | 99.2 | 97.8 | 97.4 | 96.7 | 95.9 | 95.7 | 99.2 | 92.3 | 91.1 | 94.1 | 93.1 | 91.1 | 93.1 | 97.1 | 92.4 | 96.5 | 96.4 | 92.9 | 97.7 | 98.5 | 94.5 | 98.5 | 91.1 | 98.3 | 97.7 | 96.5 | 97.4 | 96.5 | 97.6 | 99.4 | 96 | 95.9 | 95.4 | 99.6 | 91.1 | 96.7833 | 99.6 | 91.1
2026-05-09 | 17:00:00.000 | 43 | 42 | 42.2 | 42.7 | 42.2 | 41.8 | 42.1 | 44 | 43.4 | 42.8 | 42.7 | 42.5 | 42.6167 | 44 | 41.8 | 40 | 41.2 | 40.9 | 40.1 | 40.5 | 43.2 | 41.1 | 42.5 | 42.3 | 40.7 | 42.9 | 43.1 | 41.5417 | 43.2 | 40 | 43.3 | 42.7 | 42.7 | 43.1 | 42.7 | 43.4 | 44.2 | 41.5 | 42.7 | 42.2 | 43.9 | 41.2 | 42.8 | 44.2 | 41.2
2026-05-09 | 17:15:00.000 | 30.7 | 30.1 | 30.3 | 30.3 | 30.5 | 29.9 | 29.2 | 30.9 | 30.6 | 30.2 | 30.1 | 30.4 | 30.2667 | 30.9 | 29.2 | 29.7 | 30.6 | 30.4 | 30.1 | 30.9 | 32.8 | 31.7 | 33.1 | 33.3 | 32.8 | 34.9 | 35.3 | 32.1333 | 35.3 | 29.7 | 30.5 | 29.5 | 29.2 | 29.4 | 29.1 | 29.5 | 29.9 | 29.1 | 29 | 28.9 | 30.4 | 27.6 | 29.3417 | 30.5 | 27.6
2026-05-09 | 17:30:00.000 | 57.9 | 57 | 57.4 | 57.7 | 57.6 | 56.5 | 55.6 | 57.8 | 59.2 | 58.5 | 58.2 | 58 | 57.6167 | 59.2 | 55.6 | 55.3 | 57.1 | 54.6 | 55.4 | 56.2 | 61.6 | 59 | 61.6 | 61.5 | 59.7 | 63.1 | 63.5 | 59.05 | 63.5 | 54.6 | 57 | 55.7 | 55.8 | 56.3 | 56.6 | 58.1 | 58.7 | 57 | 56.7 | 55.3 | 57.3 | 51.7 | 56.35 | 58.7 | 51.7
2026-05-09 | 17:45:00.000 | 39.7 | 39.1 | 39.3 | 39.7 | 39.5 | 38.8 | 37.1 | 41.1 | 40.6 | 40.2 | 40.2 | 39.7 | 39.5833 | 41.1 | 37.1 | 37.8 | 39.2 | 38.8 | 38 | 38.3 | 42 | 40.3 | 41.9 | 41.9 | 40.5 | 42.7 | 42.9 | 40.3583 | 42.9 | 37.8 | 40 | 39.3 | 39.3 | 39.7 | 39.7 | 40.3 | 40.7 | 39.6 | 39.5 | 38.8 | 40.2 | 37.2 | 39.525 | 40.7 | 37.2
2026-05-09 | 18:00:00.000 | 15.9 | 15.6 | 15.7 | 15.8 | 15.7 | 15.4 | 15.3 | 16.4 | 16.2 | 16 | 16 | 15.8 | 15.8167 | 16.4 | 15.3 | 14.9 | 15.4 | 15.3 | 14.9 | 15.1 | 16.6 | 16 | 16.5 | 16.5 | 16 | 16.9 | 17 | 15.925 | 17 | 14.9 | 16.1 | 15.8 | 15.8 | 15.9 | 15.9 | 15.7 | 16.3 | 15.9 | 15.8 | 15.7 | 16.2 | 14.9 | 15.8333 | 16.3 | 14.9
2026-05-09 | 18:15:00.000 | 30.8 | 30.4 | 30.6 | 31 | 30.9 | 30.7 | 29.4 | 32.6 | 32.4 | 32.1 | 32 | 31.5 | 31.2 | 32.6 | 29.4 | 29.5 | 30.9 | 30.5 | 29.6 | 28.5 | 32.5 | 31.1 | 32.2 | 32.3 | 31 | 32.5 | 32.8 | 31.1167 | 32.8 | 28.5 | 32.9 | 32.3 | 32.2 | 32.3 | 32 | 32 | 32.3 | 31.6 | 32 | 30.4 | 32.7 | 28 | 31.725 | 32.9 | 28
2026-05-09 | 18:30:00.000 | 38.4 | 37.9 | 38.2 | 37.3 | 38.4 | 38.1 | 38.1 | 40.3 | 39.8 | 39.5 | 39.4 | 38.7 | 38.675 | 40.3 | 37.3 | 36.5 | 38.2 | 37.8 | 36.6 | 36.8 | 40.1 | 38.4 | 39.7 | 39.8 | 38.2 | 40.1 | 40.2 | 38.5333 | 40.2 | 36.5 | 40 | 39.4 | 39.5 | 39.7 | 39.5 | 39.6 | 40 | 39.1 | 39.4 | 39.2 | 40 | 36.4 | 39.3167 | 40 | 36.4
2026-05-09 | 18:45:00.000 | 30.6 | 30.2 | 30.4 | 30.8 | 30.5 | 30.3 | 29.6 | 32.1 | 31.8 | 30.4 | 31.4 | 29.8 | 30.6583 | 32.1 | 29.6 | 29 | 29.1 | 30 | 29.1 | 29.2 | 31.9 | 30.5 | 31.6 | 31.6 | 30.3 | 31.7 | 31.9 | 30.4917 | 31.9 | 29 | 31.8 | 31.4 | 31.5 | 31.6 | 31.5 | 31.5 | 31.8 | 31.1 | 31.4 | 31.3 | 31.9 | 29 | 31.3167 | 31.9 | 29
2026-05-09 | 19:00:00.000 | 19.5 | 19.2 | 19.4 | 19.6 | 19.4 | 19.4 | 19.2 | 20.5 | 20.2 | 20.1 | 20 | 19.6 | 19.675 | 20.5 | 19.2 | 18.4 | 19.2 | 19 | 18.4 | 18.5 | 20.3 | 19.4 | 20 | 20 | 19.2 | 20.1 | 20.3 | 19.4 | 20.3 | 18.4 | 20.3 | 19.9 | 20.1 | 20.1 | 20.1 | 20 | 20.2 | 19.8 | 20 | 20 | 20.4 | 18.5 | 19.95 | 20.4 | 18.5
2026-05-09 | 19:15:00.000 | 16.5 | 16.3 | 16.4 | 16.7 | 16.5 | 16.5 | 16.6 | 17.5 | 17.3 | 17.2 | 17.2 | 16.9 | 16.8 | 17.5 | 16.3 | 15.7 | 16.5 | 16.3 | 15.6 | 15.7 | 17.3 | 16.5 | 17 | 17 | 16.2 | 17 | 17.2 | 16.5 | 17.3 | 15.6 | 17.5 | 17.3 | 17.4 | 17.4 | 17.3 | 17.1 | 17.3 | 17 | 17.2 | 17.4 | 17.6 | 15.8 | 17.1917 | 17.6 | 15.8
2026-05-09 | 19:30:00.000 | 11 | 10.9 | 11 | 11.1 | 11 | 11.1 | 11.1 | 11.7 | 11.6 | 11.6 | 11.5 | 11.3 | 11.2417 | 11.7 | 10.9 | 10.5 | 11 | 10.9 | 10.4 | 10.5 | 11.6 | 11.2 | 11.5 | 11.5 | 10.9 | 11.5 | 11.6 | 11.0917 | 11.6 | 10.4 | 11.8 | 11.7 | 11.7 | 11.2 | 11.7 | 11 | 11.6 | 11.4 | 11.6 | 11.7 | 11.8 | 10.5 | 11.475 | 11.8 | 10.5
2026-05-09 | 19:45:00.000 | 7 | 6.6 | 6.7 | 7.1 | 7 | 7 | 7 | 7.4 | 7.3 | 7.3 | 7.2 | 7.1 | 7.0583 | 7.4 | 6.6 | 6.6 | 7 | 6.9 | 6.4 | 6.6 | 7.3 | 7.1 | 7.1 | 7.3 | 7 | 7.4 | 7.5 | 7.0167 | 7.5 | 6.4 | 7.2 | 7.3 | 7.4 | 7.3 | 7.3 | 7.2 | 7.2 | 7.2 | 7.3 | 7.4 | 7.5 | 6.6 | 7.2417 | 7.5 | 6.6
2026-05-09 | 20:00:00.000 | 3.1 | 3 | 3.1 | 3.1 | 3.1 | 3.2 | 3.1 | 3.3 | 3.3 | 3.2 | 3.3 | 3.1 | 3.1583 | 3.3 | 3 | 2.9 | 3.1 | 3.1 | 2.9 | 2.9 | 3.3 | 3.1 | 3.2 | 3.3 | 3 | 3.2 | 3.3 | 3.1083 | 3.3 | 2.9 | 3.3 | 3.1 | 3.2 | 3.1 | 3.2 | 3.1 | 3.1 | 3.2 | 3.3 | 3.3 | 3.3 | 2.9 | 3.175 | 3.3 | 2.9
2026-05-09 | 20:15:00.000 | 0.4 | 0.3 | 0.6 | 0.6 | 0.7 | 0.5 | 0.6 | 0.6 | 0.7 | 0.5 | 0.5 | 0.7 | 0.55833 | 0.7 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.6 | 0.5 | 0.6 | 0.65 | 0.8 | 0.5 | 0.9 | 0.8 | 0.7 | 0.6 | 0.7 | 0.7 | 0.5 | 0.7 | 0.6 | 0.7 | 0.8 | 0.6 | 0.69167 | 0.9 | 0.5
2026-05-09 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.15833 | 0.7 | 0.1 | 0.1 | 0.1 | 1 | 0.1 | 0.6 | 0.1 | 0.1 | 0.6 | 0.1 | 0.1 | 0.1 | 0.9 | 0.325 | 1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11667 | 0.3 | 0.1
2026-05-09 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0.5 | 0 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0.3 | 0.2 | 0.5 | 0 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0.11 | 0.2 | 0
2026-05-09 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-09 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320