## PR_Calc
PR CALCULATION
10 MAGGIO 2026 | [67 empty] | 10 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 50
RAW PR | [64 empty] | 0.76599 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 76.5987
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 76.5877
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 76.5531
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-10 | 00:00:00.000 | -0.7 | -0.000175 | -0.7 | -0.000175 | -0.000175 | 0 | -0.000175 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8517
2026-05-10 | 00:15:00.000 | -0.9 | -0.000225 | -0.7 | -0.000175 | -0.0002 | 0 | -0.0002 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 00:30:00.000 | 0 | 0 | -0.2 | -5e-05 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 00:45:00.000 | 0.5 | 0.000125 | 0 | 0 | 6.25e-05 | 0 | 6.25e-05 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 05:15:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 05:30:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 06:15:00.000 | 2.4 | 0.0006 | 2.6 | 0.00065 | 0.000625 | 0 | 0.000625 | 0.08 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 06:30:00.000 | 12.5 | 0.003125 | 12.4 | 0.0031 | 0.0031125 | 0 | 0.0031125 | 0.0080321 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 06:45:00.000 | 22.6 | 0.00565 | 22.9 | 0.005725 | 0.0056875 | 0 | 0.0056875 | 0.013187 | 30737.7 | 30737.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 07:00:00.000 | 56.6 | 0.01415 | 56.4 | 0.0141 | 0.014125 | 56.5 | 0.01415 | 0.0035398 | 30737.7 | 30737.8 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 07:15:00.000 | 105.3 | 0.026325 | 103.8 | 0.02595 | 0.026138 | 104.55 | 0.026325 | 0.014347 | 30737.8 | 30738 | 200 | 0.876 | 7.08 | 7.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 7.08 | 0 | 14.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.425 | 0 | 0 | 0 | 0 | 0 | 0.675 | 7.425 | 0 | 7.425 | 0.89245
2026-05-10 | 07:30:00.000 | 155.8 | 0.03895 | 154.5 | 0.038625 | 0.038788 | 155.15 | 0.03895 | 0.008379 | 30738 | 30738.3 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2977 | 0 | 0 | 0 | 0 | 0 | 1.0271 | 11.2977 | 0 | 11.2977 | 0.89245
2026-05-10 | 07:45:00.000 | 220.4 | 0.0551 | 220.2 | 0.05505 | 0.055075 | 220.3 | 0.0551 | 0.00090785 | 30738.3 | 30738.8 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.0068 | 0 | 0 | 0 | 0 | 0 | 1.4552 | 16.0068 | 0 | 16.0068 | 0.89245
2026-05-10 | 08:00:00.000 | 299.2 | 0.0748 | 301.1 | 0.075275 | 0.075038 | 300.15 | 0.075275 | 0.0063302 | 30738.8 | 30739.4 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 08:15:00.000 | 368.4 | 0.0921 | 370.3 | 0.092575 | 0.092337 | 369.35 | 0.092575 | 0.0051442 | 30739.4 | 30740.2 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 08:30:00.000 | 442 | 0.1105 | 447.3 | 0.11183 | 0.11116 | 444.65 | 0.11183 | 0.011919 | 30740.2 | 30741.2 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 08:45:00.000 | 520.8 | 0.1302 | 526.3 | 0.13157 | 0.13089 | 523.55 | 0.13157 | 0.010505 | 30741.2 | 30742.4 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 09:00:00.000 | 530.4 | 0.1326 | 513.8 | 0.12845 | 0.13053 | 522.1 | 0.1326 | 0.031795 | 30742.4 | 30743.7 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 09:15:00.000 | 495.3 | 0.12383 | 508.3 | 0.12707 | 0.12545 | 501.8 | 0.12707 | 0.025907 | 30743.7 | 30744.9 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 09:30:00.000 | 516.4 | 0.1291 | 523.9 | 0.13098 | 0.13004 | 520.15 | 0.13098 | 0.014419 | 30744.9 | 30746.2 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 09:45:00.000 | 550.7 | 0.13768 | 526.3 | 0.13157 | 0.13462 | 538.5 | 0.13768 | 0.045311 | 30746.2 | 30747.6 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 10:00:00.000 | 466.4 | 0.1166 | 453.4 | 0.11335 | 0.11497 | 459.9 | 0.1166 | 0.028267 | 30747.6 | 30748.9 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 10:15:00.000 | 506.8 | 0.1267 | 523.9 | 0.13098 | 0.12884 | 515.35 | 0.13098 | 0.033181 | 30748.9 | 30750.1 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 10:30:00.000 | 770.8 | 0.1927 | 733.8 | 0.18345 | 0.18807 | 752.3 | 0.1927 | 0.049183 | 30750.1 | 30751.7 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 10:45:00.000 | 781.4 | 0.19535 | 780.8 | 0.1952 | 0.19527 | 781.1 | 0.19535 | 0.00076815 | 30751.7 | 30753.6 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 11:00:00.000 | 806.9 | 0.20172 | 781.6 | 0.1954 | 0.19856 | 794.25 | 0.20172 | 0.031854 | 30753.6 | 30755.5 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 11:15:00.000 | 801.2 | 0.2003 | 804 | 0.201 | 0.20065 | 802.6 | 0.201 | 0.0034887 | 30755.5 | 30757.5 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 11:30:00.000 | 870 | 0.2175 | 846.9 | 0.21172 | 0.21461 | 858.45 | 0.2175 | 0.026909 | 30757.5 | 30759.5 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 11:45:00.000 | 813.8 | 0.20345 | 783.9 | 0.19597 | 0.19971 | 798.85 | 0.20345 | 0.037429 | 30759.5 | 30761.5 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 12:00:00.000 | 777.7 | 0.19443 | 769.1 | 0.19228 | 0.19335 | 773.4 | 0.19443 | 0.01112 | 30761.5 | 30763.4 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 12:15:00.000 | 835.5 | 0.20888 | 810 | 0.2025 | 0.20569 | 822.75 | 0.20888 | 0.030994 | 30763.4 | 30765.4 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 12:30:00.000 | 826.3 | 0.20657 | 813.2 | 0.2033 | 0.20494 | 819.75 | 0.20657 | 0.01598 | 30765.4 | 30767.4 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 12:45:00.000 | 898.6 | 0.22465 | 873.9 | 0.21848 | 0.22156 | 886.25 | 0.22465 | 0.02787 | 30767.4 | 30769.5 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 13:00:00.000 | 905.9 | 0.22647 | 877.5 | 0.21937 | 0.22292 | 891.7 | 0.22647 | 0.031849 | 30769.5 | 30771.6 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 13:15:00.000 | 907.8 | 0.22695 | 882.5 | 0.22062 | 0.22379 | 895.15 | 0.22695 | 0.028263 | 30771.6 | 30773.8 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 13:30:00.000 | 920.2 | 0.23005 | 896.1 | 0.22403 | 0.22704 | 908.15 | 0.23005 | 0.026537 | 30773.8 | 30776 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 13:45:00.000 | 929.3 | 0.23232 | 904.3 | 0.22607 | 0.2292 | 916.8 | 0.23232 | 0.027269 | 30776 | 30778.1 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 14:00:00.000 | 914.1 | 0.22853 | 886 | 0.2215 | 0.22501 | 900.05 | 0.22853 | 0.03122 | 30778.1 | 30780.3 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 14:15:00.000 | 927.2 | 0.2318 | 898.4 | 0.2246 | 0.2282 | 912.8 | 0.2318 | 0.031551 | 30780.3 | 30782.5 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 14:30:00.000 | 926.8 | 0.2317 | 899.4 | 0.22485 | 0.22828 | 913.1 | 0.2317 | 0.030008 | 30782.5 | 30784.6 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 14:45:00.000 | 933.7 | 0.23343 | 904.6 | 0.22615 | 0.22979 | 919.15 | 0.23343 | 0.03166 | 30784.6 | 30786.8 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 15:00:00.000 | 954.3 | 0.23857 | 921.7 | 0.23043 | 0.2345 | 938 | 0.23857 | 0.034755 | 30786.8 | 30789 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 15:15:00.000 | 969.2 | 0.2423 | 934.5 | 0.23362 | 0.23796 | 951.85 | 0.2423 | 0.036455 | 30789 | 30791.2 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 15:30:00.000 | 972.1 | 0.24303 | 937.3 | 0.23432 | 0.23867 | 954.7 | 0.24303 | 0.036451 | 30791.2 | 30793.4 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 15:45:00.000 | 965.2 | 0.2413 | 929.9 | 0.23247 | 0.23689 | 947.55 | 0.2413 | 0.037254 | 30793.4 | 30795.7 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 16:00:00.000 | 968 | 0.242 | 937.4 | 0.23435 | 0.23817 | 952.7 | 0.242 | 0.032119 | 30795.7 | 30797.9 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 16:15:00.000 | 975.5 | 0.24388 | 942.4 | 0.2356 | 0.23974 | 958.95 | 0.24388 | 0.034517 | 30797.9 | 30800.1 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 16:30:00.000 | 962.7 | 0.24068 | 931.2 | 0.2328 | 0.23674 | 946.95 | 0.24068 | 0.033265 | 30800.1 | 30802.3 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 16:45:00.000 | 962.8 | 0.2407 | 921.9 | 0.23047 | 0.23559 | 942.35 | 0.2407 | 0.043402 | 30802.3 | 30804.5 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 17:00:00.000 | 957.3 | 0.23932 | 931.5 | 0.23287 | 0.2361 | 944.4 | 0.23932 | 0.027319 | 30804.5 | 30806.7 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 17:15:00.000 | 929.6 | 0.2324 | 922 | 0.2305 | 0.23145 | 925.8 | 0.2324 | 0.0082091 | 30806.7 | 30808.9 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 17:30:00.000 | 827.3 | 0.20682 | 868.4 | 0.2171 | 0.21196 | 847.85 | 0.2171 | 0.048476 | 30808.9 | 30810.9 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 17:45:00.000 | 724.8 | 0.1812 | 775.4 | 0.19385 | 0.18752 | 750.1 | 0.19385 | 0.067458 | 30810.9 | 30812.8 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 18:00:00.000 | 616.8 | 0.1542 | 679.5 | 0.16987 | 0.16204 | 648.15 | 0.16987 | 0.096737 | 30812.8 | 30814.3 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 18:15:00.000 | 523 | 0.13075 | 581.6 | 0.1454 | 0.13808 | 552.3 | 0.1454 | 0.1061 | 30814.3 | 30815.7 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 18:30:00.000 | 416 | 0.104 | 476.4 | 0.1191 | 0.11155 | 446.2 | 0.1191 | 0.13537 | 30815.7 | 30816.8 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 18:45:00.000 | 320 | 0.08 | 369.5 | 0.092375 | 0.086188 | 344.75 | 0.092375 | 0.14358 | 30816.8 | 30817.6 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 19:00:00.000 | 197 | 0.04925 | 245.7 | 0.061425 | 0.055337 | 221.35 | 0.061425 | 0.22001 | 30817.6 | 30818.2 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 19:15:00.000 | 76.9 | 0.019225 | 84.6 | 0.02115 | 0.020188 | 80.75 | 0.02115 | 0.095356 | 30818.2 | 30818.6 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 19:30:00.000 | 38.6 | 0.00965 | 55.3 | 0.013825 | 0.011737 | 0 | 0.011737 | 0.3557 | 30818.6 | 30818.7 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 19:45:00.000 | 21 | 0.00525 | 22.4 | 0.0056 | 0.005425 | 0 | 0.005425 | 0.064516 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 20:00:00.000 | 9.6 | 0.0024 | 9.2 | 0.0023 | 0.00235 | 0 | 0.00235 | 0.042553 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 20:15:00.000 | 1.2 | 0.0003 | 1.2 | 0.0003 | 0.0003 | 0 | 0.0003 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 20:30:00.000 | -0.6 | -0.00015 | -0.7 | -0.000175 | -0.0001625 | 0 | -0.0001625 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 21:00:00.000 | -0.1 | -2.5e-05 | -0.1 | -2.5e-05 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 21:30:00.000 | -0.2 | -5e-05 | -0.1 | -2.5e-05 | -3.75e-05 | 0 | -3.75e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 21:45:00.000 | -1.4 | -0.00035 | -1.3 | -0.000325 | -0.0003375 | 0 | -0.0003375 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 22:00:00.000 | -0.9 | -0.000225 | -0.8 | -0.0002 | -0.0002125 | 0 | -0.0002125 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 22:15:00.000 | -0.6 | -0.00015 | -0.4 | -0.0001 | -0.000125 | 0 | -0.000125 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 22:30:00.000 | -1.9 | -0.000475 | -1.8 | -0.00045 | -0.0004625 | 0 | -0.0004625 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 22:45:00.000 | -2.3 | -0.000575 | -2 | -0.0005 | -0.0005375 | 0 | -0.0005375 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 23:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 23:15:00.000 | -1.5 | -0.000375 | -1.1 | -0.000275 | -0.000325 | 0 | -0.000325 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 23:30:00.000 | -0.3 | -7.5e-05 | -0.1 | -2.5e-05 | -5e-05 | 0 | -5e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
2026-05-10 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89245
PR for each inverter |  |  | 8.5486 |  | 8.4701 | 8.5093 |  | 8.6596 |  |  |  | 81000 |  | 0.73259 | 0.73945 | 0.7424 | 0.76074 | 0.76206 | 0.74298 | 0.74923 | 0.76429 | 0.76739 | 0.75923 | 0.7761 | 0.7873 | #DIV/0! | #DIV/0! | #DIV/0! | 14.16 | 0.77752 | 0.76918 | 0.75571 | 0.7636 | 0.76509 | 0.7739 | 0.79327 | 0.7938 | 0.79664 | 0.79353 | 0.80159 | 0.80743 |  |  |  | 0 | 0.79564 | 0.76635 | 0.76476 | 0.75525 | 0.7616 | 0.75171 | 0.76715 | 0.74437 | 0.74916 | 0.73989 | 0.7568 | 0.74387 | #DIV/0! | #DIV/0! | #DIV/0! | 34.7295 |  | 0.76588 |  | #DIV/0! | #DIV/0! | 7.3291e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-10 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 06:30:00.000 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.5 | 0 | 0 | 0 | 2.7 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 2.4 | 2.275 | 2.7 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0
2026-05-10 | 06:45:00.000 | 1.4 | 1.2 | 1.8 | 1.9 | 5.5 | 1.5 | 1.7 | 2.7 | 2.5 | 1.9 | 2.1 | 3 | 2.2667 | 5.5 | 1.2 | 2.7 | 2.4 | 5.2 | 2.1 | 5.1 | 2.3 | 3 | 5.8 | 3.2 | 3 | 2.9 | 6 | 3.6417 | 6 | 2.1 | 6 | 2.2 | 2.1 | 2.2 | 2.6 | 2.8 | 2.7 | 2.2 | 2.3 | 2.1 | 2.7 | 2.3 | 2.6833 | 6 | 2.1
2026-05-10 | 07:00:00.000 | 5.9 | 6.4 | 5.1 | 13.9 | 5 | 13.8 | 13.9 | 14.9 | 14.8 | 14.5 | 14.6 | 14.7 | 11.4583 | 14.9 | 5 | 13.9 | 14.2 | 14.9 | 13.3 | 14.6 | 15 | 15 | 16.4 | 15.1 | 14.7 | 15.2 | 16.8 | 14.925 | 16.8 | 13.3 | 15.5 | 14.2 | 14.2 | 14.4 | 14.8 | 15 | 4.2 | 14.7 | 4.4 | 14.4 | 15.1 | 13.6 | 12.875 | 15.5 | 4.2
2026-05-10 | 07:15:00.000 | 0 | 0 | 23.6 | 28.9 | 28.8 | 28.2 | 28.2 | 30.1 | 29.9 | 27.2 | 28.9 | 29.4 | 28.32 | 30.1 | 0 | 27.8 | 28.5 | 28.3 | 27.7 | 27.6 | 30.3 | 29.8 | 30.8 | 31.2 | 29.6 | 31.2 | 31.4 | 29.5167 | 31.4 | 27.6 | 31 | 29.7 | 30 | 30.4 | 30.6 | 30.7 | 0 | 30 | 26.6 | 29.3 | 30.6 | 27.8 | 29.7 | 31 | 0
2026-05-10 | 07:30:00.000 | 32 | 29.7 | 43 | 43.5 | 43.4 | 42.5 | 42.7 | 45.5 | 43.3 | 44.9 | 45.7 | 44.4 | 41.7167 | 45.7 | 29.7 | 42 | 43 | 42.7 | 41.8 | 41.7 | 45.8 | 45 | 46.6 | 47.2 | 44.7 | 47 | 47.3 | 44.5667 | 47.3 | 41.7 | 46.6 | 44.7 | 45.3 | 46 | 46.2 | 46.2 | 0 | 45.1 | 45.3 | 44.1 | 46 | 41.6 | 45.1909 | 46.6 | 0
2026-05-10 | 07:45:00.000 | 58.9 | 60.5 | 61.3 | 62.1 | 62.1 | 60.8 | 61.3 | 65 | 64.2 | 64.2 | 65.3 | 63.2 | 62.4083 | 65.3 | 58.9 | 60.2 | 61.3 | 61.3 | 59.6 | 59.3 | 63.1 | 64.2 | 66.4 | 67.1 | 63.6 | 66.6 | 66.8 | 63.2917 | 67.1 | 59.3 | 65.7 | 63.4 | 64.4 | 65.2 | 65.6 | 65.4 | 0 | 64.1 | 64.2 | 62.5 | 65.1 | 58.7 | 64.0273 | 65.7 | 0
2026-05-10 | 08:00:00.000 | 80.2 | 79.4 | 81 | 81.6 | 81.6 | 79.7 | 79.9 | 85.1 | 84.2 | 84.4 | 86.2 | 83.6 | 82.2417 | 86.2 | 79.4 | 78.9 | 79.7 | 80 | 78 | 77.3 | 86.2 | 84.7 | 87.6 | 88.1 | 83.6 | 87.3 | 87.7 | 83.2583 | 88.1 | 77.3 | 84.6 | 82 | 83.6 | 84.5 | 84.4 | 84.5 | 66.9 | 83.6 | 82.9 | 79.3 | 83.9 | 75.3 | 81.2917 | 84.6 | 66.9
2026-05-10 | 08:15:00.000 | 91.7 | 88.9 | 94.1 | 96.1 | 96.2 | 94.1 | 94.6 | 99.9 | 99.6 | 99.6 | 102.7 | 100.4 | 96.4917 | 102.7 | 88.9 | 94 | 95.4 | 95.6 | 93 | 91.8 | 103.4 | 102.4 | 106 | 106.5 | 100.7 | 106.1 | 106.3 | 100.1 | 106.5 | 91.8 | 98.9 | 97.8 | 99.4 | 99.4 | 99.9 | 98.9 | 100.3 | 97.7 | 96.8 | 93.7 | 94.6 | 85 | 96.8667 | 100.3 | 85
2026-05-10 | 08:30:00.000 | 111.5 | 111.5 | 113.3 | 116.1 | 116.4 | 113.3 | 114.9 | 121 | 120.7 | 120.3 | 124.1 | 121 | 117.0083 | 124.1 | 111.5 | 114.2 | 116.7 | 116.2 | 112.3 | 111 | 124.8 | 123.3 | 128.2 | 128.3 | 121.3 | 127.6 | 128.1 | 121 | 128.3 | 111 | 123.9 | 119.2 | 120.4 | 120.5 | 121.3 | 119.7 | 122 | 118.2 | 117.9 | 114.6 | 119.2 | 107 | 118.6583 | 123.9 | 107
2026-05-10 | 08:45:00.000 | 134.4 | 134 | 135.8 | 139.5 | 139.7 | 136.1 | 138.4 | 145.4 | 145 | 144 | 148.3 | 144.6 | 140.4333 | 148.3 | 134 | 137.5 | 141.3 | 139.7 | 134.5 | 133.2 | 150 | 147.4 | 153.1 | 152.8 | 144.4 | 151.9 | 152.7 | 144.875 | 153.1 | 133.2 | 147.9 | 143.2 | 139 | 144 | 145.4 | 142.8 | 146.3 | 136 | 141.3 | 138 | 142.6 | 128.4 | 141.2417 | 147.9 | 128.4
2026-05-10 | 09:00:00.000 | 142.8 | 141.6 | 142.1 | 149 | 146.4 | 143.2 | 148.3 | 151.1 | 149.7 | 149.9 | 152.5 | 143.4 | 146.6667 | 152.5 | 141.6 | 146.1 | 150.3 | 146.8 | 141.4 | 140.4 | 151.7 | 143.5 | 157.1 | 155.6 | 145.7 | 152.6 | 153.7 | 148.7417 | 157.1 | 140.4 | 149.4 | 145.7 | 147.3 | 145.5 | 145.4 | 142.7 | 147.2 | 137.7 | 143.9 | 141.9 | 136.8 | 134.2 | 143.1417 | 149.4 | 134.2
2026-05-10 | 09:15:00.000 | 134.6 | 129.3 | 134.3 | 137.9 | 138.7 | 135.3 | 136.7 | 145.2 | 146 | 143.6 | 147.7 | 144.7 | 139.5 | 147.7 | 129.3 | 137.1 | 141.5 | 138.8 | 133.1 | 132.3 | 151.1 | 146.7 | 155 | 153.6 | 145 | 153.2 | 149.9 | 144.775 | 155 | 132.3 | 153 | 147.3 | 147.2 | 146 | 147.3 | 143.8 | 147.6 | 141.7 | 142.4 | 135.3 | 144.7 | 127.2 | 143.625 | 153 | 127.2
2026-05-10 | 09:30:00.000 | 136.8 | 135.8 | 131.5 | 137.3 | 142.8 | 137.2 | 137.7 | 152.3 | 153.8 | 146.7 | 148.9 | 150.6 | 142.6167 | 153.8 | 131.5 | 139.8 | 145 | 139.6 | 137.4 | 137.6 | 153.9 | 150.3 | 161.5 | 154 | 150.5 | 155.8 | 158.7 | 148.675 | 161.5 | 137.4 | 152 | 147.3 | 151.3 | 147 | 150.1 | 147.2 | 148.3 | 147.8 | 149.5 | 147.2 | 150.1 | 130.7 | 147.375 | 152 | 130.7
2026-05-10 | 09:45:00.000 | 147.5 | 147.5 | 150.5 | 154.5 | 156.2 | 151.6 | 156.7 | 159.8 | 159.1 | 159.6 | 160.8 | 157 | 155.0667 | 160.8 | 147.5 | 152.3 | 158.6 | 155 | 148.9 | 147.8 | 160.3 | 156.3 | 163.8 | 163.5 | 154 | 164.1 | 165.8 | 157.5333 | 165.8 | 147.8 | 159.1 | 155.3 | 150.3 | 153.1 | 152.7 | 146.8 | 147.7 | 148.2 | 149.1 | 139.8 | 146.6 | 141 | 149.1417 | 159.1 | 139.8
2026-05-10 | 10:00:00.000 | 127.9 | 127.7 | 128.5 | 131.3 | 132.2 | 128 | 129.9 | 136.7 | 135.9 | 133.2 | 135.8 | 134 | 131.7583 | 136.7 | 127.7 | 129.3 | 132.6 | 129.8 | 124.5 | 121.2 | 136 | 135.2 | 140.2 | 138.9 | 132.5 | 134.5 | 142.1 | 133.0667 | 142.1 | 121.2 | 138.3 | 133.3 | 134.5 | 132 | 132.5 | 130.7 | 137.3 | 132.7 | 132.1 | 128.9 | 130.7 | 122.9 | 132.1583 | 138.3 | 122.9
2026-05-10 | 10:15:00.000 | 129.8 | 131.4 | 131.9 | 133.8 | 135.9 | 136.5 | 134.6 | 146.8 | 151.8 | 147.4 | 151.4 | 150 | 140.1083 | 151.8 | 129.8 | 138.6 | 142.3 | 138.8 | 135.9 | 139.4 | 155.6 | 152.8 | 154.8 | 152 | 151.1 | 160 | 162.7 | 148.6667 | 162.7 | 135.9 | 154.9 | 148 | 149.1 | 145.8 | 148.4 | 145.1 | 151.8 | 144.2 | 144.6 | 143.6 | 147.4 | 119.7 | 145.2167 | 154.9 | 119.7
2026-05-10 | 10:30:00.000 | 198.4 | 199.1 | 200.1 | 208.5 | 203.4 | 203 | 202.7 | 212.2 | 214 | 208.6 | 206.7 | 209.1 | 205.4833 | 214 | 198.4 | 199.8 | 208.2 | 203.7 | 195.6 | 194.9 | 212.3 | 213 | 222.3 | 212.6 | 210.9 | 226.7 | 228.7 | 210.725 | 228.7 | 194.9 | 214 | 209.9 | 202.1 | 202.2 | 200.5 | 202.4 | 209.4 | 194.8 | 201.3 | 199.1 | 204.2 | 185.6 | 202.125 | 214 | 185.6
2026-05-10 | 10:45:00.000 | 196.8 | 199.2 | 201.4 | 208.7 | 207.9 | 201.9 | 200.6 | 219.7 | 216.2 | 217.7 | 213.7 | 218.3 | 208.5083 | 219.7 | 196.8 | 202.5 | 209.9 | 208.4 | 199.7 | 200 | 228.7 | 223.4 | 234.5 | 233 | 222.2 | 237.1 | 239.7 | 219.925 | 239.7 | 199.7 | 231.1 | 224.2 | 220.9 | 222.8 | 217.4 | 215.1 | 209.7 | 210.8 | 211.8 | 210.6 | 218.9 | 187.4 | 215.0583 | 231.1 | 187.4
2026-05-10 | 11:00:00.000 | 211.5 | 210.8 | 211.8 | 214.6 | 215.1 | 208.2 | 212.6 | 223.4 | 222.5 | 221.9 | 226.9 | 220.5 | 216.65 | 226.9 | 208.2 | 208.6 | 216.4 | 212 | 206 | 203.4 | 227.7 | 223.7 | 233.5 | 234 | 223.3 | 236.7 | 241.6 | 222.2417 | 241.6 | 203.4 | 224.6 | 221.1 | 220.6 | 210.2 | 222.8 | 220 | 224.6 | 215.2 | 215.3 | 211 | 210.6 | 203.7 | 216.6417 | 224.6 | 203.7
2026-05-10 | 11:15:00.000 | 198.9 | 209.1 | 207.5 | 212.2 | 214.4 | 206.6 | 212.1 | 224.7 | 228.1 | 225 | 232.2 | 224.1 | 216.2417 | 232.2 | 198.9 | 211.3 | 220.4 | 215.9 | 209.8 | 210.9 | 235.6 | 226.4 | 238.8 | 241.7 | 233.1 | 245.4 | 244.6 | 227.825 | 245.4 | 209.8 | 233 | 222.5 | 231.5 | 217 | 223.2 | 217.8 | 225.7 | 218.5 | 203.5 | 219.3 | 223.5 | 201.9 | 219.7833 | 233 | 201.9
2026-05-10 | 11:30:00.000 | 219.1 | 221.5 | 226.3 | 231.7 | 229.2 | 223.4 | 227 | 242.3 | 235.2 | 242.4 | 244.7 | 244.3 | 232.2583 | 244.7 | 219.1 | 225.3 | 235 | 230.5 | 223.5 | 220.9 | 251.7 | 247 | 254.2 | 256.9 | 245 | 257.3 | 258.5 | 242.15 | 258.5 | 220.9 | 240.6 | 227.9 | 237.6 | 237.1 | 237.4 | 233.7 | 242.5 | 235.1 | 236.7 | 214.2 | 235.7 | 202.9 | 231.7833 | 242.5 | 202.9
2026-05-10 | 11:45:00.000 | 210.3 | 208.3 | 216.8 | 215.2 | 219.3 | 210.2 | 208 | 222.3 | 221.2 | 226.3 | 225.2 | 226.4 | 217.4583 | 226.4 | 208 | 209 | 219.4 | 214.1 | 206.7 | 206.3 | 226.2 | 218.7 | 232.8 | 237 | 225.7 | 240.1 | 232.1 | 222.3417 | 240.1 | 206.3 | 230.6 | 221.8 | 216.7 | 220.3 | 211.6 | 221.8 | 221.8 | 219.7 | 219.3 | 214.2 | 220 | 199.5 | 218.1083 | 230.6 | 199.5
2026-05-10 | 12:00:00.000 | 192.6 | 196.7 | 199.9 | 207.3 | 208.8 | 205 | 208.9 | 217.3 | 218.8 | 207.6 | 221.2 | 217.1 | 208.4333 | 221.2 | 192.6 | 195.9 | 207.9 | 212.6 | 204.8 | 206.4 | 228.3 | 212 | 232 | 231.8 | 222.3 | 233.7 | 226.4 | 217.8417 | 233.7 | 195.9 | 217.7 | 205.1 | 217.2 | 205.8 | 207.3 | 193.6 | 203.7 | 208.8 | 210 | 207.3 | 211.3 | 172.4 | 205.0167 | 217.7 | 172.4
2026-05-10 | 12:15:00.000 | 217 | 219 | 217.1 | 223.6 | 221 | 217.9 | 208.8 | 228.2 | 231.1 | 228 | 223.3 | 223.5 | 221.5417 | 231.1 | 208.8 | 211.6 | 220.6 | 219 | 207.1 | 212.9 | 232.7 | 226.5 | 239 | 239.9 | 225.6 | 239.7 | 242.7 | 226.4417 | 242.7 | 207.1 | 245.3 | 230.6 | 234.2 | 228.8 | 233.9 | 221.3 | 231.4 | 223.2 | 216.3 | 217 | 228.5 | 205.3 | 226.3167 | 245.3 | 205.3
2026-05-10 | 12:30:00.000 | 210.1 | 209.4 | 209.9 | 218 | 216.4 | 209.8 | 221.2 | 228 | 226.5 | 231.5 | 238.2 | 230 | 220.75 | 238.2 | 209.4 | 222.2 | 232.2 | 229.2 | 223.6 | 223.8 | 235 | 230.2 | 243.1 | 233.1 | 229.4 | 248.8 | 250.9 | 233.4583 | 250.9 | 222.2 | 230.1 | 224.3 | 227.3 | 220.7 | 218.9 | 224.1 | 227.8 | 213.2 | 220.9 | 219.3 | 227.3 | 194.6 | 220.7083 | 230.1 | 194.6
2026-05-10 | 12:45:00.000 | 228.6 | 231.4 | 230 | 237.9 | 234.2 | 231.2 | 227.4 | 244.1 | 246.2 | 242 | 248.7 | 241.8 | 236.9583 | 248.7 | 227.4 | 228.2 | 235.7 | 234 | 224.1 | 225.9 | 246.9 | 247.1 | 258 | 258.8 | 246.5 | 261.2 | 263 | 244.1167 | 263 | 224.1 | 257.9 | 245 | 247.3 | 246.8 | 250 | 246.5 | 248.8 | 239.9 | 240.7 | 236 | 245.2 | 215.7 | 243.3167 | 257.9 | 215.7
2026-05-10 | 13:00:00.000 | 230 | 232.7 | 233.1 | 236.8 | 239.6 | 231.8 | 233.6 | 248.8 | 246.9 | 247.7 | 252.2 | 245.4 | 239.8833 | 252.2 | 230 | 231 | 238.8 | 236.2 | 228.1 | 228.8 | 252.6 | 249.1 | 260 | 262.2 | 250.1 | 264.4 | 265.4 | 247.225 | 265.4 | 228.1 | 260.2 | 248.2 | 250.5 | 244.7 | 245.7 | 240.7 | 248.7 | 241.1 | 242.1 | 238.3 | 244.5 | 220.6 | 243.775 | 260.2 | 220.6
2026-05-10 | 13:15:00.000 | 230.7 | 232.9 | 232.3 | 237.1 | 238 | 230.8 | 233.8 | 247.9 | 248.7 | 246.8 | 251 | 245 | 239.5833 | 251 | 230.7 | 230.7 | 237.9 | 234.6 | 227.1 | 219.5 | 250.7 | 247.8 | 258.3 | 260.8 | 240.5 | 262.2 | 264.6 | 244.5583 | 264.6 | 219.5 | 259.6 | 248.5 | 249 | 246.8 | 248.3 | 244.9 | 250.1 | 242.9 | 243.9 | 238.7 | 245.9 | 221.1 | 244.975 | 259.6 | 221.1
2026-05-10 | 13:30:00.000 | 232.4 | 234.7 | 234.8 | 238.8 | 240.5 | 233.1 | 235.9 | 250.7 | 251.2 | 249.4 | 254 | 247.6 | 241.925 | 254 | 232.4 | 233.5 | 240.8 | 237 | 230 | 231.2 | 254 | 249.9 | 260.7 | 263.3 | 251.7 | 266.3 | 267.9 | 248.8583 | 267.9 | 230 | 262.7 | 251.9 | 251.7 | 249.3 | 251.4 | 247.4 | 253.5 | 245.7 | 246.7 | 241.7 | 249.7 | 223.4 | 247.925 | 262.7 | 223.4
2026-05-10 | 13:45:00.000 | 233.4 | 235.9 | 235.7 | 240.3 | 241.5 | 234.4 | 236.3 | 251.9 | 252.5 | 250 | 254.8 | 248.6 | 242.9417 | 254.8 | 233.4 | 234.7 | 242.3 | 229.9 | 230.2 | 231.7 | 255.6 | 250.9 | 261.5 | 263.8 | 252.1 | 267.4 | 268.2 | 249.025 | 268.2 | 229.9 | 264.1 | 253.1 | 244.3 | 250.4 | 252.6 | 248.3 | 254.7 | 246.6 | 248 | 243.1 | 250.7 | 224.7 | 248.3833 | 264.1 | 224.7
2026-05-10 | 14:00:00.000 | 229 | 231.4 | 231.2 | 236.1 | 236.5 | 230.3 | 233 | 245 | 247.5 | 235.2 | 249.4 | 242.4 | 237.25 | 249.4 | 229 | 230.8 | 238.2 | 233.8 | 225.8 | 227 | 250.2 | 245.5 | 255.8 | 257.2 | 245.9 | 260.4 | 261.7 | 244.3583 | 261.7 | 225.8 | 257.4 | 246.8 | 247 | 244 | 246.3 | 242.1 | 248.9 | 241 | 242.4 | 237.7 | 244.5 | 220.3 | 243.2 | 257.4 | 220.3
2026-05-10 | 14:15:00.000 | 231.7 | 233.8 | 233.6 | 238.6 | 239.1 | 232.6 | 235.5 | 242.8 | 250.6 | 242.3 | 252.6 | 242.2 | 239.6167 | 252.6 | 231.7 | 225.4 | 241 | 236.4 | 228.5 | 229 | 253.3 | 248.8 | 259.7 | 261.4 | 249.3 | 263.7 | 265.7 | 246.85 | 265.7 | 225.4 | 260.7 | 250.4 | 250.4 | 247.6 | 250.1 | 245.6 | 252 | 243.8 | 245.4 | 241 | 247.3 | 223 | 246.4417 | 260.7 | 223
2026-05-10 | 14:30:00.000 | 223.9 | 232.8 | 233.4 | 237.9 | 237.3 | 232.6 | 235.5 | 241.9 | 251.2 | 240 | 253.3 | 240.4 | 238.35 | 253.3 | 223.9 | 233.3 | 241 | 234.7 | 228.3 | 228.8 | 252.6 | 249.6 | 260.3 | 262.8 | 250.4 | 265.1 | 266.5 | 247.7833 | 266.5 | 228.3 | 260.8 | 249.4 | 249.6 | 247.7 | 250.3 | 245.3 | 252.4 | 244.4 | 245.5 | 240.8 | 246.8 | 221.7 | 246.225 | 260.8 | 221.7
2026-05-10 | 14:45:00.000 | 231.6 | 233.6 | 233.2 | 238.4 | 239.1 | 232.6 | 234.8 | 241.4 | 250.6 | 241.8 | 253.4 | 241.5 | 239.3333 | 253.4 | 231.6 | 233.6 | 241.4 | 236.6 | 227.9 | 228.2 | 254 | 248.9 | 260.9 | 263 | 250.2 | 263.3 | 265.2 | 247.7667 | 265.2 | 227.9 | 261.5 | 251.1 | 250.6 | 248.7 | 251.4 | 247 | 253.6 | 245.1 | 238.8 | 242.1 | 247.3 | 223.4 | 246.7167 | 261.5 | 223.4
2026-05-10 | 15:00:00.000 | 235.1 | 237.4 | 237.1 | 242.2 | 243.1 | 236.8 | 239.4 | 255.1 | 255.9 | 253.1 | 257.6 | 250 | 245.2333 | 257.6 | 235.1 | 237.9 | 246 | 240.6 | 224.1 | 232.7 | 259.1 | 254 | 265.1 | 267 | 254.8 | 259.5 | 270.8 | 250.9667 | 270.8 | 224.1 | 255.9 | 255.8 | 254.9 | 252.3 | 255.4 | 251.1 | 258.2 | 249.2 | 249.5 | 247.1 | 252 | 227.2 | 250.7167 | 258.2 | 227.2
2026-05-10 | 15:15:00.000 | 238.1 | 240.3 | 240.1 | 245.1 | 246.1 | 239.9 | 242.4 | 258.7 | 258.7 | 256.7 | 261.2 | 253.4 | 248.3917 | 261.2 | 238.1 | 240.6 | 249.1 | 243.5 | 235.2 | 235.4 | 261.6 | 257 | 259.8 | 270.5 | 257.9 | 272.2 | 274.6 | 254.7833 | 274.6 | 235.2 | 268.5 | 258.8 | 258.1 | 254.8 | 258.4 | 254.2 | 252.1 | 252.3 | 254 | 250.3 | 246 | 230.3 | 253.15 | 268.5 | 230.3
2026-05-10 | 15:30:00.000 | 238.5 | 240.7 | 240.1 | 245 | 237.9 | 240 | 242.4 | 258.6 | 258.8 | 256.4 | 261 | 253.3 | 247.725 | 261 | 237.9 | 240.3 | 248.3 | 243.3 | 235 | 227.2 | 260.3 | 255.5 | 266.6 | 269.6 | 257.4 | 270.9 | 275.1 | 254.125 | 275.1 | 227.2 | 268.1 | 258.7 | 248 | 246.4 | 258.2 | 254.1 | 261.3 | 251.3 | 252.7 | 248.4 | 254.8 | 230.4 | 252.7 | 268.1 | 230.4
2026-05-10 | 15:45:00.000 | 237.1 | 239.2 | 238.6 | 243.1 | 244.1 | 237.8 | 240 | 247.2 | 248 | 255.3 | 260 | 252.2 | 245.2167 | 260 | 237.1 | 238.3 | 246.3 | 241.5 | 232.9 | 233.1 | 260.2 | 255.3 | 267.3 | 269.3 | 256.6 | 271 | 273.2 | 253.75 | 273.2 | 232.9 | 267 | 256.3 | 255.7 | 253 | 256 | 252.5 | 259.7 | 250.7 | 252.5 | 249.3 | 253.5 | 229.2 | 252.95 | 267 | 229.2
2026-05-10 | 16:00:00.000 | 236.3 | 231 | 239.1 | 243.3 | 243.9 | 238.6 | 241.4 | 256.8 | 258 | 254.6 | 260.8 | 253.2 | 246.4167 | 260.8 | 231 | 238.4 | 247.4 | 233.6 | 233.9 | 234.3 | 261.2 | 256.5 | 267.4 | 269.6 | 257.2 | 272.8 | 275.7 | 254 | 275.7 | 233.6 | 259.3 | 258.2 | 247.8 | 245.1 | 247.8 | 253 | 260.5 | 250.9 | 253.3 | 250.4 | 254.7 | 230 | 250.9167 | 260.5 | 230
2026-05-10 | 16:15:00.000 | 237.6 | 240.7 | 240.8 | 245.2 | 245.9 | 240.3 | 242.9 | 259.2 | 260 | 257.1 | 262.4 | 254.5 | 248.8833 | 262.4 | 237.6 | 239.8 | 248.4 | 243.2 | 234.8 | 235.2 | 262.2 | 257.2 | 269 | 271.6 | 259 | 273.9 | 275.4 | 255.8083 | 275.4 | 234.8 | 269.3 | 257.2 | 257.3 | 255.1 | 257 | 253.9 | 261.1 | 252.3 | 254.3 | 251 | 255.6 | 230.8 | 254.575 | 269.3 | 230.8
2026-05-10 | 16:30:00.000 | 225.6 | 236.8 | 236.8 | 240.9 | 242.6 | 236.2 | 238.8 | 255 | 255.8 | 254 | 259.1 | 251.1 | 244.3917 | 259.1 | 225.6 | 235.9 | 244.3 | 239.4 | 231.3 | 232.3 | 258.6 | 254 | 266 | 268.2 | 255.7 | 271.2 | 273.6 | 252.5417 | 273.6 | 231.3 | 265.8 | 253.6 | 253.3 | 251.5 | 253.6 | 250.1 | 256.4 | 239.5 | 249.8 | 246.3 | 251.2 | 227 | 249.8417 | 265.8 | 227
2026-05-10 | 16:45:00.000 | 234.8 | 238.5 | 237.3 | 241.8 | 243.2 | 237.3 | 239.8 | 255.1 | 254.9 | 253 | 257.3 | 250.7 | 245.3083 | 257.3 | 234.8 | 235.3 | 244 | 238.9 | 231.6 | 229.9 | 254.3 | 249.3 | 262.8 | 263.3 | 251.2 | 268.8 | 269.8 | 249.9333 | 269.8 | 229.9 | 261 | 251.3 | 250.3 | 248.8 | 251.1 | 248.6 | 243.9 | 242.6 | 244.9 | 240.7 | 245.7 | 226.2 | 246.2583 | 261 | 226.2
2026-05-10 | 17:00:00.000 | 231.5 | 234.9 | 227.1 | 238.4 | 239.8 | 233.8 | 235.5 | 252.6 | 253.5 | 251.6 | 256.3 | 249.2 | 242.0167 | 256.3 | 227.1 | 232 | 240.3 | 235.8 | 228.3 | 229.7 | 255.8 | 251.3 | 263.1 | 265.9 | 253.6 | 269 | 271.3 | 249.675 | 271.3 | 228.3 | 264.1 | 252.5 | 251.9 | 250.8 | 253 | 249.5 | 256.1 | 238 | 249.3 | 245.6 | 250.6 | 226.1 | 248.9583 | 264.1 | 226.1
2026-05-10 | 17:15:00.000 | 225.9 | 229.3 | 229.4 | 232.4 | 234.2 | 228.6 | 231.9 | 248.3 | 249.3 | 247.8 | 252.4 | 239.7 | 237.4333 | 252.4 | 225.9 | 224.8 | 232.5 | 228.5 | 220.6 | 222.3 | 246.4 | 241 | 250.2 | 253.7 | 240.3 | 253 | 254.3 | 238.9667 | 254.3 | 220.6 | 260.5 | 248.2 | 247.7 | 246.8 | 248.4 | 245.2 | 252.1 | 242.9 | 245.4 | 241.4 | 247.4 | 222.6 | 245.7167 | 260.5 | 222.6
2026-05-10 | 17:30:00.000 | 203.1 | 206.5 | 206.2 | 209.1 | 210.7 | 205.7 | 211 | 227 | 228 | 226.4 | 230.8 | 216.7 | 215.1 | 230.8 | 203.1 | 201.4 | 208.8 | 204.9 | 196.6 | 198.3 | 220.3 | 208.2 | 223.6 | 227.2 | 214.9 | 225.6 | 226.6 | 213.0333 | 227.2 | 196.6 | 244.6 | 233.8 | 233.1 | 232.1 | 230.8 | 227 | 234.4 | 225.7 | 229 | 227.9 | 232.3 | 206.1 | 229.7333 | 244.6 | 206.1
2026-05-10 | 17:45:00.000 | 177.3 | 180.4 | 179.7 | 182.9 | 184.3 | 179.2 | 182 | 199.4 | 200.4 | 198.8 | 202.9 | 189.1 | 188.0333 | 202.9 | 177.3 | 175.8 | 182.5 | 178.8 | 170.8 | 172.7 | 191.8 | 188.9 | 195 | 198.4 | 187.2 | 196.2 | 194.3 | 186.0333 | 198.4 | 170.8 | 215.8 | 207.4 | 206.1 | 203.2 | 201.3 | 198.1 | 205.2 | 197.8 | 201.5 | 202.1 | 204.3 | 179.7 | 201.875 | 215.8 | 179.7
2026-05-10 | 18:00:00.000 | 151 | 153.7 | 152.8 | 155.8 | 152 | 152.1 | 151 | 170.5 | 171.3 | 170 | 173.6 | 161.5 | 159.6083 | 173.6 | 151 | 150 | 155.4 | 152.9 | 145.4 | 147.2 | 163 | 161.1 | 166.1 | 168.7 | 158.3 | 165.4 | 164.2 | 158.1417 | 168.7 | 145.4 | 185.8 | 180 | 178.6 | 174.1 | 173.4 | 171.1 | 178 | 171.5 | 174.9 | 175.6 | 175.7 | 155 | 174.475 | 185.8 | 155
2026-05-10 | 18:15:00.000 | 127.5 | 129.9 | 128.9 | 131.2 | 132.7 | 127.2 | 122.4 | 144.9 | 145.4 | 144.5 | 147.8 | 136.5 | 134.9083 | 147.8 | 122.4 | 125.1 | 129.4 | 127.4 | 120.6 | 122 | 135.9 | 134.8 | 138.7 | 140.9 | 132.2 | 138.2 | 139.9 | 132.0917 | 140.9 | 120.6 | 159.1 | 154.5 | 151.7 | 140.5 | 145.3 | 143.5 | 149.8 | 144.5 | 148.3 | 150.5 | 147.9 | 129.6 | 147.1 | 159.1 | 129.6
2026-05-10 | 18:30:00.000 | 100.1 | 102.1 | 101.6 | 103.8 | 105 | 100.1 | 95 | 115.6 | 116.2 | 115.1 | 118.4 | 108.4 | 106.7833 | 118.4 | 95 | 99.5 | 102.7 | 101.6 | 95.8 | 96.6 | 106.2 | 106.1 | 108.8 | 110.1 | 103.1 | 107.6 | 108.5 | 103.8833 | 110.1 | 95.8 | 122.3 | 123.7 | 120.5 | 114.6 | 115 | 114.8 | 119.9 | 115.9 | 119.1 | 120.9 | 118 | 104.8 | 117.4583 | 123.7 | 104.8
2026-05-10 | 18:45:00.000 | 76.7 | 78.1 | 76.9 | 78.7 | 79.5 | 71 | 70.1 | 88.5 | 88.3 | 83.2 | 88.6 | 79.4 | 79.9167 | 88.6 | 70.1 | 73.6 | 75.9 | 75.6 | 70.8 | 71.5 | 76 | 75.9 | 77.5 | 78.1 | 72.6 | 76 | 76.2 | 74.975 | 78.1 | 70.8 | 94.1 | 92.4 | 89.6 | 84 | 85.1 | 87 | 91.6 | 88.6 | 91.6 | 93 | 89.5 | 81.6 | 89.0083 | 94.1 | 81.6
2026-05-10 | 19:00:00.000 | 46.3 | 47.1 | 47.4 | 49.4 | 51.8 | 48 | 47.7 | 54.5 | 55.8 | 55.2 | 56.8 | 52.7 | 51.0583 | 56.8 | 46.3 | 49 | 51 | 50.3 | 46.9 | 47.9 | 49.4 | 50.6 | 51.5 | 52 | 48.3 | 49.3 | 49.7 | 49.6583 | 52 | 46.9 | 60.2 | 58.1 | 56.5 | 54.2 | 55.7 | 57.9 | 57.8 | 54.1 | 55.8 | 56.9 | 53.2 | 51.5 | 55.9917 | 60.2 | 51.5
2026-05-10 | 19:15:00.000 | 17.6 | 18.2 | 18.4 | 20.3 | 22.1 | 20.9 | 22.2 | 21.3 | 22.1 | 22.1 | 22.9 | 22 | 20.8417 | 22.9 | 17.6 | 22 | 23.4 | 23.5 | 21.8 | 22.2 | 20.3 | 20.6 | 21.8 | 21.8 | 20.2 | 21.1 | 21.6 | 21.6917 | 23.5 | 20.2 | 20.7 | 19.6 | 18.5 | 16.8 | 16.6 | 16.8 | 17.6 | 17.2 | 18.4 | 19.4 | 19.1 | 15.2 | 17.9917 | 20.7 | 15.2
2026-05-10 | 19:30:00.000 | 8 | 8.1 | 8 | 8.3 | 8.4 | 8.3 | 8.8 | 9.6 | 9.8 | 9.8 | 9.9 | 9.4 | 8.8667 | 9.9 | 8 | 8.5 | 9.1 | 8.9 | 8.3 | 8.4 | 9.2 | 9.4 | 9.7 | 9.8 | 9 | 9.5 | 9.8 | 9.1333 | 9.8 | 8.3 | 12.4 | 11.6 | 11 | 10.4 | 10.1 | 9.7 | 10 | 9.7 | 10.5 | 11.2 | 10.7 | 8.2 | 10.4583 | 12.4 | 8.2
2026-05-10 | 19:45:00.000 | 4.7 | 4.5 | 4.5 | 4.5 | 4.5 | 4.4 | 4.3 | 4.9 | 4.9 | 4.9 | 4.9 | 4.7 | 4.6417 | 4.9 | 4.3 | 4.2 | 4.3 | 4.3 | 4.1 | 4 | 4.8 | 4.8 | 5 | 5.1 | 4.8 | 5.1 | 5.2 | 4.6417 | 5.2 | 4 | 5.4 | 5.2 | 5.4 | 5.3 | 5.6 | 5.5 | 5.7 | 5.5 | 5.6 | 5.4 | 5.3 | 5.4 | 5.4417 | 5.7 | 5.2
2026-05-10 | 20:00:00.000 | 2.2 | 2.1 | 2.2 | 2.3 | 2.2 | 2.3 | 2.2 | 2.4 | 2.4 | 2.4 | 2.4 | 2.3 | 2.2833 | 2.4 | 2.1 | 2.1 | 2.2 | 2.1 | 2 | 2 | 2.3 | 2.4 | 2.5 | 2.5 | 2.3 | 2.5 | 2.5 | 2.2833 | 2.5 | 2 | 2.4 | 2.2 | 2.4 | 2.3 | 2.4 | 2.3 | 2.4 | 2.4 | 2.5 | 2.3 | 2.4 | 2.2 | 2.35 | 2.5 | 2.2
2026-05-10 | 20:15:00.000 | 0.5 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.9 | 0.8 | 0.9 | 0.8 | 0.6 | 0.8 | 0.7 | 0.9 | 0.3 | 0.7 | 0.8 | 0.5 | 0.9 | 0.8 | 0.9 | 0.9 | 0.7 | 1 | 0.8 | 0.7 | 0.6 | 0.775 | 1 | 0.5 | 0.7 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.9 | 0.8 | 0.8 | 0.8 | 0.6 | 0.825 | 1 | 0.6
2026-05-10 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.14167 | 0.4 | 0.1 | 0.1 | 0.1 | 0.9 | 0.1 | 0.7 | 0.1 | 0.1 | 0.8 | 0.1 | 0.1 | 0.1 | 0.9 | 0.34167 | 0.9 | 0.1 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.125 | 0.2 | 0.1
2026-05-10 | 20:45:00.000 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.12 | 0.2 | 0 | 0.1 | 0.1 | 0.7 | 0.1 | 0.4 | 0.1 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.5 | 0.23333 | 0.7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-10 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.15 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-10 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320