## PR_Calc
PR CALCULATION
11 MAGGIO 2026 | [67 empty] | 11 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 51
RAW PR | [64 empty] | 0.77382 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 77.382
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 77.3688
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 77.3407
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-11 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8748.9
2026-05-11 | 00:15:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 00:30:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 00:45:00.000 | -1 | -0.00025 | -0.5 | -0.000125 | -0.0001875 | 0 | -0.0001875 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 01:00:00.000 | -1.8 | -0.00045 | -1.6 | -0.0004 | -0.000425 | 0 | -0.000425 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 01:15:00.000 | -1.9 | -0.000475 | -1.8 | -0.00045 | -0.0004625 | 0 | -0.0004625 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 01:30:00.000 | -1.5 | -0.000375 | -1 | -0.00025 | -0.0003125 | 0 | -0.0003125 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 01:45:00.000 | -2 | -0.0005 | -1.1 | -0.000275 | -0.0003875 | 0 | -0.0003875 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 02:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 02:15:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 02:30:00.000 | -1.6 | -0.0004 | -1.5 | -0.000375 | -0.0003875 | 0 | -0.0003875 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 02:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 03:00:00.000 | -1.3 | -0.000325 | -0.7 | -0.000175 | -0.00025 | 0 | -0.00025 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 03:15:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 03:30:00.000 | -0.6 | -0.00015 | -0.1 | -2.5e-05 | -8.75e-05 | 0 | -8.75e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 03:45:00.000 | -0.9 | -0.000225 | -0.8 | -0.0002 | -0.0002125 | 0 | -0.0002125 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 04:00:00.000 | -0.9 | -0.000225 | -0.2 | -5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 04:15:00.000 | -1.3 | -0.000325 | -1 | -0.00025 | -0.0002875 | 0 | -0.0002875 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 04:30:00.000 | -2 | -0.0005 | -1 | -0.00025 | -0.000375 | 0 | -0.000375 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 04:45:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 05:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 05:15:00.000 | -0.3 | -7.5e-05 | -0.2 | -5e-05 | -6.25e-05 | 0 | -6.25e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 05:30:00.000 | 0.6 | 0.00015 | 0.9 | 0.000225 | 0.0001875 | 0 | 0.0001875 | 0.4 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 05:45:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 06:00:00.000 | -0.1 | -2.5e-05 | 0.1 | 2.5e-05 | 0 | 0 | 0 | 0 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 06:15:00.000 | 5.4 | 0.00135 | 5.7 | 0.001425 | 0.0013875 | 0 | 0.0013875 | 0.054054 | 30818.7 | 30818.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 06:30:00.000 | 18.1 | 0.004525 | 18.3 | 0.004575 | 0.00455 | 0 | 0.00455 | 0.010989 | 30818.7 | 30818.8 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 06:45:00.000 | 39.9 | 0.009975 | 40.6 | 0.01015 | 0.010063 | 0 | 0.010063 | 0.017391 | 30818.8 | 30818.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 07:00:00.000 | 60.6 | 0.01515 | 62.1 | 0.015525 | 0.015338 | 61.35 | 0.015525 | 0.02445 | 30818.8 | 30818.9 | 100 | 0.876 | 0 | 0 | 4.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33693 | 4.0432 | 0 | 4.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4136 | 0 | 0 | 0 | 0 | 0 | 0.40124 | 4.4136 | 0 | 4.4136 | 0.90117
2026-05-11 | 07:15:00.000 | 97 | 0.02425 | 98.2 | 0.02455 | 0.0244 | 97.6 | 0.02455 | 0.012295 | 30818.9 | 30819.1 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2114 | 0 | 0 | 0 | 0 | 0 | 0.65558 | 7.2114 | 0 | 7.2114 | 0.90117
2026-05-11 | 07:30:00.000 | 111.4 | 0.02785 | 110.2 | 0.02755 | 0.0277 | 110.8 | 0.02785 | 0.01083 | 30819.1 | 30819.4 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3614 | 0 | 0 | 0 | 0 | 0 | 0.76012 | 8.3614 | 0 | 8.3614 | 0.90117
2026-05-11 | 07:45:00.000 | 118.3 | 0.029575 | 116.1 | 0.029025 | 0.0293 | 117.2 | 0.029575 | 0.018771 | 30819.4 | 30819.7 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8159 | 0 | 0 | 0 | 0 | 0 | 0.80145 | 8.8159 | 0 | 8.8159 | 0.90117
2026-05-11 | 08:00:00.000 | 159.8 | 0.03995 | 157.2 | 0.0393 | 0.039625 | 158.5 | 0.03995 | 0.016404 | 30819.7 | 30820.1 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9364 | 0 | 0 | 0 | 0 | 0 | 1.0851 | 11.9364 | 0 | 11.9364 | 0.90117
2026-05-11 | 08:15:00.000 | 430.3 | 0.10758 | 432 | 0.108 | 0.10779 | 431.15 | 0.108 | 0.0039429 | 30820.1 | 30820.9 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 08:30:00.000 | 445.8 | 0.11145 | 439.1 | 0.10978 | 0.11061 | 442.45 | 0.11145 | 0.015143 | 30820.9 | 30822 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 08:45:00.000 | 671.5 | 0.16787 | 686.3 | 0.17157 | 0.16972 | 678.9 | 0.17157 | 0.0218 | 30822 | 30823.3 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 09:00:00.000 | 857 | 0.21425 | 853.8 | 0.21345 | 0.21385 | 855.4 | 0.21425 | 0.0037409 | 30823.3 | 30825.1 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 09:15:00.000 | 810.1 | 0.20253 | 801.5 | 0.20037 | 0.20145 | 805.8 | 0.20253 | 0.010673 | 30825.1 | 30827.2 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 09:30:00.000 | 587.7 | 0.14693 | 587.4 | 0.14685 | 0.14689 | 587.55 | 0.14693 | 0.00051059 | 30827.2 | 30829 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 09:45:00.000 | 488.4 | 0.1221 | 480.6 | 0.12015 | 0.12113 | 484.5 | 0.1221 | 0.016099 | 30829 | 30830.3 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 10:00:00.000 | 458.4 | 0.1146 | 452.6 | 0.11315 | 0.11388 | 455.5 | 0.1146 | 0.012733 | 30830.3 | 30831.5 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 10:15:00.000 | 734.6 | 0.18365 | 723.4 | 0.18085 | 0.18225 | 729 | 0.18365 | 0.015364 | 30831.5 | 30833 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 10:30:00.000 | 542.5 | 0.13562 | 536.8 | 0.1342 | 0.13491 | 539.65 | 0.13562 | 0.010562 | 30833 | 30834.5 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 10:45:00.000 | 749.2 | 0.1873 | 747.7 | 0.18693 | 0.18711 | 748.45 | 0.1873 | 0.0020041 | 30834.5 | 30836 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 11:00:00.000 | 776.7 | 0.19418 | 759 | 0.18975 | 0.19196 | 767.85 | 0.19418 | 0.023051 | 30836 | 30838.1 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 11:15:00.000 | 542.6 | 0.13565 | 534.7 | 0.13368 | 0.13466 | 538.65 | 0.13565 | 0.014666 | 30838.1 | 30839.5 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 11:30:00.000 | 837.2 | 0.2093 | 818.1 | 0.20453 | 0.20691 | 827.65 | 0.2093 | 0.023077 | 30839.5 | 30841.2 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 11:45:00.000 | 897.9 | 0.22448 | 876.1 | 0.21902 | 0.22175 | 887 | 0.22448 | 0.024577 | 30841.2 | 30843.3 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 12:00:00.000 | 941.6 | 0.2354 | 924.7 | 0.23118 | 0.23329 | 933.15 | 0.2354 | 0.018111 | 30843.3 | 30845.5 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 12:15:00.000 | 952.2 | 0.23805 | 923.9 | 0.23097 | 0.23451 | 938.05 | 0.23805 | 0.030169 | 30845.5 | 30847.8 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 12:30:00.000 | 861.4 | 0.21535 | 841.6 | 0.2104 | 0.21287 | 851.5 | 0.21535 | 0.023253 | 30847.8 | 30849.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 12:45:00.000 | 991.5 | 0.24788 | 966.2 | 0.24155 | 0.24471 | 978.85 | 0.24788 | 0.025847 | 30849.9 | 30852.1 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 13:00:00.000 | 966 | 0.2415 | 939.7 | 0.23493 | 0.23821 | 952.85 | 0.2415 | 0.027601 | 30852.1 | 30854.4 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 13:15:00.000 | 944.8 | 0.2362 | 920.7 | 0.23018 | 0.23319 | 932.75 | 0.2362 | 0.025838 | 30854.4 | 30856.6 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 13:30:00.000 | 978.8 | 0.2447 | 951.6 | 0.2379 | 0.2413 | 965.2 | 0.2447 | 0.028181 | 30856.6 | 30858.9 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 13:45:00.000 | 964.6 | 0.24115 | 940.6 | 0.23515 | 0.23815 | 952.6 | 0.24115 | 0.025194 | 30858.9 | 30861.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 14:00:00.000 | 974.7 | 0.24368 | 949.8 | 0.23745 | 0.24056 | 962.25 | 0.24368 | 0.025877 | 30861.2 | 30863.4 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 14:15:00.000 | 980.2 | 0.24505 | 955.9 | 0.23897 | 0.24201 | 968.05 | 0.24505 | 0.025102 | 30863.4 | 30865.7 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 14:30:00.000 | 980.9 | 0.24522 | 954.5 | 0.23863 | 0.24193 | 967.7 | 0.24522 | 0.027281 | 30865.7 | 30868 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 14:45:00.000 | 984.1 | 0.24602 | 887.1 | 0.22177 | 0.2339 | 935.6 | 0.24602 | 0.10368 | 30868 | 30870.3 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 15:00:00.000 | 986.6 | 0.24665 | 864.1 | 0.21602 | 0.23134 | 925.35 | 0.24665 | 0.13238 | 30870.3 | 30872.6 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 15:15:00.000 | 984.7 | 0.24618 | 834.8 | 0.2087 | 0.22744 | 909.75 | 0.24618 | 0.16477 | 30872.6 | 30874.8 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 15:30:00.000 | 985.3 | 0.24632 | 801.8 | 0.20045 | 0.22339 | 893.55 | 0.24632 | 0.20536 | 30874.8 | 30877.1 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 15:45:00.000 | 982.9 | 0.24572 | 740.7 | 0.18518 | 0.21545 | 861.8 | 0.24572 | 0.28104 | 30877.1 | 30879.4 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 16:00:00.000 | 980.2 | 0.24505 | 929.6 | 0.2324 | 0.23873 | 954.9 | 0.24505 | 0.05299 | 30879.4 | 30881.7 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 16:15:00.000 | 974.4 | 0.2436 | 953.2 | 0.2383 | 0.24095 | 963.8 | 0.2436 | 0.021996 | 30881.7 | 30883.9 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 16:30:00.000 | 965.9 | 0.24147 | 947.2 | 0.2368 | 0.23914 | 956.55 | 0.24147 | 0.019549 | 30883.9 | 30886.1 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 16:45:00.000 | 951.1 | 0.23778 | 934.2 | 0.23355 | 0.23566 | 942.65 | 0.23778 | 0.017928 | 30886.1 | 30888.3 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 17:00:00.000 | 935.5 | 0.23387 | 919.8 | 0.22995 | 0.23191 | 927.65 | 0.23387 | 0.016924 | 30888.3 | 30890.5 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 17:15:00.000 | 753.3 | 0.18832 | 744.8 | 0.1862 | 0.18726 | 749.05 | 0.18832 | 0.011348 | 30890.5 | 30892.5 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 17:30:00.000 | 782.5 | 0.19562 | 829 | 0.20725 | 0.20144 | 805.75 | 0.20725 | 0.05771 | 30892.5 | 30894.3 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 17:45:00.000 | 693.9 | 0.17347 | 750.8 | 0.1877 | 0.18059 | 722.35 | 0.1877 | 0.078771 | 30894.3 | 30896.1 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 18:00:00.000 | 563.6 | 0.1409 | 624.2 | 0.15605 | 0.14848 | 593.9 | 0.15605 | 0.10204 | 30896.1 | 30897.6 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 18:15:00.000 | 437.8 | 0.10945 | 493.1 | 0.12328 | 0.11636 | 465.45 | 0.12328 | 0.11881 | 30897.6 | 30898.8 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 18:30:00.000 | 277.9 | 0.069475 | 318.1 | 0.079525 | 0.0745 | 298 | 0.079525 | 0.1349 | 30898.8 | 30899.6 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 18:45:00.000 | 271.1 | 0.067775 | 321.3 | 0.080325 | 0.07405 | 296.2 | 0.080325 | 0.16948 | 30899.6 | 30900.3 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 19:00:00.000 | 180.6 | 0.04515 | 223 | 0.05575 | 0.05045 | 201.8 | 0.05575 | 0.21011 | 30900.3 | 30900.9 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 19:15:00.000 | 101.9 | 0.025475 | 133.7 | 0.033425 | 0.02945 | 117.8 | 0.033425 | 0.26995 | 30900.9 | 30901.2 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 19:30:00.000 | 71.3 | 0.017825 | 99.2 | 0.0248 | 0.021312 | 85.25 | 0.0248 | 0.32727 | 30901.2 | 30901.4 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 19:45:00.000 | 41.6 | 0.0104 | 56.3 | 0.014075 | 0.012237 | 0 | 0.012237 | 0.30031 | 30901.4 | 30901.5 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 20:00:00.000 | 16.9 | 0.004225 | 16.4 | 0.0041 | 0.0041625 | 0 | 0.0041625 | 0.03003 | 30901.5 | 30901.6 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 20:15:00.000 | 2 | 0.0005 | 1.7 | 0.000425 | 0.0004625 | 0 | 0.0004625 | 0.16216 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 20:30:00.000 | -2.3 | -0.000575 | -2.4 | -0.0006 | -0.0005875 | 0 | -0.0005875 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 20:45:00.000 | -2.1 | -0.000525 | -2.4 | -0.0006 | -0.0005625 | 0 | -0.0005625 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 21:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 21:15:00.000 | -2 | -0.0005 | -1.9 | -0.000475 | -0.0004875 | 0 | -0.0004875 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 21:30:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 21:45:00.000 | -1.3 | -0.000325 | -1 | -0.00025 | -0.0002875 | 0 | -0.0002875 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 22:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 22:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 22:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 22:45:00.000 | -1 | -0.00025 | -0.2 | -5e-05 | -0.00015 | 0 | -0.00015 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 23:00:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 23:15:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 23:30:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
2026-05-11 | 23:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30901.6 | 30901.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90117
PR for each inverter |  |  | 8.7144 |  | 8.4992 | 8.6068 |  | 8.8254 |  |  |  | 82900 |  | 0.74126 | 0.74659 | 0.75056 | 0.76755 | 0.76871 | 0.75387 | 0.7647 | 0.77461 | 0.77693 | 0.76529 | 0.78187 | 0.79182 | #DIV/0! | #DIV/0! | #DIV/0! | 4.0432 | 0.7848 | 0.77666 | 0.76288 | 0.77034 | 0.7689 | 0.7803 | 0.79612 | 0.79282 | 0.79549 | 0.79451 | 0.80069 | 0.80476 |  |  |  | 0 | 0.8272 | 0.8083 | 0.77047 | 0.76226 | 0.76179 | 0.75395 | 0.76809 | 0.7526 | 0.7573 | 0.74302 | 0.78392 | 0.75184 | #DIV/0! | #DIV/0! | #DIV/0! | 40.7386 |  | 0.77369 |  | #DIV/0! | #DIV/0! | 7.1834e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-11 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.46667 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 06:30:00.000 | 0.3 | 0.3 | 0.6 | 0.6 | 2.6 | 0.5 | 0.6 | 0.9 | 0.9 | 0.5 | 0.7 | 1 | 0.79167 | 2.6 | 0.3 | 0.9 | 0.8 | 4.2 | 0.8 | 4.1 | 0.8 | 1.1 | 3 | 1 | 0.9 | 0.9 | 5 | 1.9583 | 5 | 0.8 | 3.4 | 0.8 | 0.8 | 0.8 | 1.1 | 1 | 0.9 | 0.9 | 1 | 0.7 | 0.9 | 1 | 1.1083 | 3.4 | 0.7
2026-05-11 | 06:45:00.000 | 6 | 6.3 | 5.8 | 10.2 | 4.9 | 10.1 | 9.7 | 10.7 | 10.6 | 10.7 | 10.6 | 10.3 | 8.825 | 10.7 | 4.9 | 9.7 | 10.1 | 10.9 | 9.8 | 9.6 | 10.7 | 10.3 | 10.9 | 11.2 | 10.4 | 11 | 11 | 10.4667 | 11.2 | 9.6 | 10.9 | 10.4 | 10.1 | 10.5 | 10.6 | 10.6 | 5.5 | 10.5 | 5.6 | 10.3 | 10.8 | 9.7 | 9.625 | 10.9 | 5.5
2026-05-11 | 07:00:00.000 | 11.4 | 11 | 0 | 17.4 | 13.4 | 17.1 | 17.1 | 18.3 | 18.2 | 18.1 | 18.2 | 17.7 | 16.1727 | 18.3 | 0 | 16.7 | 17.4 | 17.1 | 16.6 | 16.6 | 18.3 | 18 | 18.7 | 18.9 | 17.9 | 18.9 | 19.1 | 17.85 | 19.1 | 16.6 | 18.7 | 17.9 | 18.1 | 18.2 | 18.5 | 18.3 | 0 | 18 | 13.5 | 18 | 18.4 | 16.6 | 17.6545 | 18.7 | 0
2026-05-11 | 07:15:00.000 | 27.3 | 27.2 | 17.1 | 28 | 27.9 | 27.5 | 27.5 | 29.2 | 29 | 28.8 | 29.3 | 28.5 | 27.275 | 29.3 | 17.1 | 27 | 27.9 | 27.7 | 27 | 27 | 29.4 | 28.9 | 30.1 | 30.5 | 28.9 | 30.5 | 30.7 | 28.8 | 30.7 | 27 | 30.1 | 28.6 | 29 | 29.1 | 29.4 | 29.3 | 0 | 28.7 | 29 | 28.3 | 29.5 | 26.3 | 28.8455 | 30.1 | 0
2026-05-11 | 07:30:00.000 | 32.1 | 32.3 | 32.9 | 34 | 34.2 | 34.1 | 34.6 | 35 | 35.3 | 35.1 | 35.8 | 34.9 | 34.1917 | 35.8 | 32.1 | 33.9 | 35.3 | 35 | 33.9 | 33.9 | 36 | 35.2 | 36.6 | 37 | 35.2 | 37.2 | 37.3 | 35.5417 | 37.3 | 33.9 | 35.6 | 34 | 33.9 | 33.6 | 33.7 | 33.2 | 0 | 32.9 | 33.4 | 33.1 | 34.3 | 30.2 | 33.4455 | 35.6 | 0
2026-05-11 | 07:45:00.000 | 34.3 | 34 | 33.9 | 34.6 | 34.3 | 33.7 | 34.1 | 36.1 | 35.6 | 35.1 | 35.4 | 34.6 | 34.6417 | 36.1 | 33.7 | 33 | 34.4 | 33.8 | 32.7 | 32.6 | 35.5 | 34.7 | 35.8 | 36 | 34.2 | 35.9 | 35.9 | 34.5417 | 36 | 32.6 | 35.7 | 34.8 | 35.1 | 35.4 | 36 | 35.8 | 0 | 35.3 | 35.5 | 35 | 35.5 | 33.8 | 35.2636 | 36 | 0
2026-05-11 | 08:00:00.000 | 46.7 | 46.1 | 46.3 | 47.3 | 47.3 | 46.8 | 48.3 | 49.4 | 49 | 49 | 49.8 | 49 | 47.9167 | 49.8 | 46.1 | 47.7 | 49.9 | 49.9 | 48.6 | 49.6 | 51.4 | 50.8 | 53.7 | 54.9 | 52.9 | 56.1 | 57.6 | 51.925 | 57.6 | 47.7 | 49.7 | 47.7 | 47.6 | 47.6 | 48.1 | 47.8 | 0 | 47.7 | 47.8 | 46.7 | 47.9 | 46.6 | 47.7455 | 49.7 | 0
2026-05-11 | 08:15:00.000 | 116.8 | 115.9 | 116 | 125.7 | 132.5 | 136 | 138 | 123.5 | 132 | 135.4 | 142.9 | 138.6 | 129.4417 | 142.9 | 115.9 | 137.2 | 140.1 | 139.2 | 135 | 131.9 | 148.8 | 145.9 | 151.4 | 151.5 | 142.4 | 147.6 | 148.4 | 143.2833 | 151.5 | 131.9 | 124.3 | 118.3 | 119.2 | 116.7 | 111.3 | 104.8 | 13.4 | 112 | 114 | 110.2 | 121.9 | 104.1 | 105.85 | 124.3 | 13.4
2026-05-11 | 08:30:00.000 | 104.7 | 110.9 | 119.2 | 139.9 | 161.4 | 161.6 | 136.4 | 129.2 | 152.7 | 162.6 | 167 | 155.6 | 141.7667 | 167 | 104.7 | 128.1 | 124.1 | 118.4 | 111.7 | 108.1 | 149.9 | 133.5 | 130.6 | 126 | 116.1 | 121.3 | 121.1 | 124.075 | 149.9 | 108.1 | 145.7 | 126.5 | 120.8 | 109.5 | 107.1 | 108.7 | 111.6 | 106.6 | 105 | 104.6 | 117.8 | 100.8 | 113.725 | 145.7 | 100.8
2026-05-11 | 08:45:00.000 | 175.5 | 170.5 | 173.6 | 174 | 172.9 | 171.9 | 175.6 | 181 | 171.6 | 172.6 | 176.6 | 168.8 | 173.7167 | 181 | 168.8 | 167.5 | 171.5 | 168.6 | 160.7 | 156.5 | 169.7 | 167.1 | 173.4 | 173.7 | 163.9 | 172.1 | 171.3 | 168 | 173.7 | 156.5 | 161 | 157.8 | 171.4 | 182.3 | 178 | 181.1 | 183.7 | 178.3 | 176.9 | 171.3 | 178.4 | 152.7 | 172.7417 | 183.7 | 152.7
2026-05-11 | 09:00:00.000 | 218.5 | 222.3 | 221.7 | 225.3 | 218.9 | 215.4 | 220.2 | 237.9 | 232.8 | 232 | 238.9 | 233.7 | 226.4667 | 238.9 | 215.4 | 217.3 | 223.5 | 222.2 | 217.5 | 217.7 | 243.2 | 238.1 | 249.2 | 241.3 | 238.3 | 252.4 | 250.4 | 234.2583 | 252.4 | 217.3 | 246.6 | 242 | 239.5 | 238.2 | 238.8 | 232.5 | 243 | 225.7 | 233.9 | 221.8 | 235.6 | 213.1 | 234.225 | 246.6 | 213.1
2026-05-11 | 09:15:00.000 | 210.2 | 211.3 | 216 | 218.1 | 218.9 | 217 | 217.7 | 233.9 | 231 | 227.4 | 232.9 | 224.1 | 221.5417 | 233.9 | 210.2 | 217.1 | 223.4 | 220.3 | 209.5 | 208.1 | 234.8 | 225.7 | 237.3 | 236.5 | 223.6 | 236.1 | 238 | 225.8667 | 238 | 208.1 | 234.1 | 226.8 | 228.9 | 227.1 | 229.4 | 226.8 | 232.8 | 212.9 | 224.8 | 222.1 | 224.7 | 204.3 | 224.5583 | 234.1 | 204.3
2026-05-11 | 09:30:00.000 | 157.2 | 156.8 | 158.2 | 160.5 | 162 | 152 | 161.5 | 171.1 | 170.4 | 169.3 | 172.2 | 165.6 | 163.0667 | 172.2 | 152 | 158.4 | 156.5 | 160.4 | 153.3 | 152.8 | 174.2 | 168 | 176.1 | 175.6 | 165.8 | 174.2 | 176.9 | 166.0167 | 176.9 | 152.8 | 176 | 171.9 | 168.9 | 170.4 | 168.1 | 163.6 | 174.8 | 168.9 | 166.8 | 162.7 | 170 | 141 | 166.925 | 176 | 141
2026-05-11 | 09:45:00.000 | 132.8 | 132.8 | 129.4 | 137.8 | 132.5 | 136 | 137.5 | 144.8 | 143.2 | 141.9 | 145.9 | 141.7 | 138.025 | 145.9 | 129.4 | 136.1 | 139.7 | 138.5 | 132 | 130.7 | 145.7 | 142.3 | 144.1 | 148.5 | 141.3 | 142.3 | 145.2 | 140.5333 | 148.5 | 130.7 | 145.8 | 140.4 | 141.7 | 138.9 | 140 | 139.1 | 143.4 | 139.2 | 133.9 | 137.1 | 140.4 | 127.7 | 138.9667 | 145.8 | 127.7
2026-05-11 | 10:00:00.000 | 125 | 124.2 | 125.6 | 128.8 | 127.7 | 126.4 | 128.9 | 134.9 | 134.2 | 132.3 | 135.9 | 132.7 | 129.7167 | 135.9 | 124.2 | 126.3 | 131.4 | 128.7 | 123.8 | 123 | 136.4 | 134.2 | 140 | 134 | 131.9 | 139.4 | 140.8 | 132.4917 | 140.8 | 123 | 135.8 | 128.8 | 131.4 | 130.7 | 127.4 | 130.2 | 135.8 | 129.8 | 129.5 | 127 | 132.2 | 118.6 | 129.7667 | 135.8 | 118.6
2026-05-11 | 10:15:00.000 | 194.1 | 193.7 | 193.5 | 200.1 | 197.8 | 193.9 | 191.3 | 210.7 | 212.9 | 200 | 208.2 | 206.3 | 200.2083 | 212.9 | 191.3 | 188.1 | 204.3 | 199.3 | 192.3 | 191.9 | 206.2 | 207.2 | 217.5 | 215.3 | 197.4 | 216.9 | 217.7 | 204.5083 | 217.7 | 188.1 | 216.3 | 205 | 208 | 204.5 | 205.2 | 204.3 | 208.3 | 201.7 | 206.4 | 203.1 | 203.2 | 188.5 | 204.5417 | 216.3 | 188.5
2026-05-11 | 10:30:00.000 | 137.3 | 146.1 | 143.2 | 150.1 | 142.3 | 143.2 | 138.7 | 155.5 | 156.3 | 150.8 | 153.7 | 155.9 | 147.7583 | 156.3 | 137.3 | 139.1 | 150.3 | 147.5 | 135.7 | 140.4 | 159.2 | 147.7 | 155.3 | 154.3 | 152.4 | 157.7 | 159.4 | 149.9167 | 159.4 | 135.7 | 158 | 149.2 | 155.7 | 153.7 | 155.5 | 152.7 | 155.3 | 143 | 150.3 | 143.1 | 143.8 | 138.4 | 149.8917 | 158 | 138.4
2026-05-11 | 10:45:00.000 | 191 | 193.8 | 191.3 | 197.7 | 189 | 190.1 | 193.3 | 207.2 | 208.3 | 203.4 | 200 | 206 | 197.5917 | 208.3 | 189 | 189.7 | 197.6 | 195.7 | 185.7 | 185.6 | 206.7 | 197.2 | 214.6 | 215.5 | 205.4 | 210.9 | 214.1 | 201.5583 | 215.5 | 185.6 | 216.6 | 200.1 | 208.9 | 207.1 | 211.1 | 208.3 | 199.3 | 204.9 | 208.3 | 201.3 | 205.7 | 183 | 204.55 | 216.6 | 183
2026-05-11 | 11:00:00.000 | 200.7 | 198.8 | 210.5 | 200.3 | 210.1 | 207.8 | 206.6 | 221.8 | 215.8 | 205.3 | 221.1 | 208.4 | 208.9333 | 221.8 | 198.8 | 207.4 | 211.3 | 210.6 | 204.6 | 196.1 | 222.1 | 214.8 | 221.1 | 217.9 | 210.4 | 222.1 | 217.9 | 213.025 | 222.1 | 196.1 | 221.8 | 210.8 | 217.5 | 207.8 | 208.1 | 204.5 | 214 | 211.4 | 215.2 | 212.7 | 207.4 | 191.4 | 210.2167 | 221.8 | 191.4
2026-05-11 | 11:15:00.000 | 142.6 | 142.4 | 142.5 | 140.5 | 146.5 | 142.8 | 146.8 | 146.1 | 154.9 | 152.1 | 154.4 | 145.6 | 146.4333 | 154.9 | 140.5 | 137.8 | 151.6 | 145.1 | 142.3 | 141.5 | 156.1 | 154.9 | 157.8 | 160.9 | 153.1 | 160.6 | 161.7 | 151.95 | 161.7 | 137.8 | 150.7 | 151.3 | 151.2 | 148.5 | 152.2 | 147.8 | 153 | 149.5 | 149.1 | 126.6 | 149.8 | 134.3 | 147 | 153 | 126.6
2026-05-11 | 11:30:00.000 | 211.6 | 212.8 | 207.8 | 210.4 | 219.4 | 214.1 | 217.4 | 231.4 | 229.4 | 228.3 | 222.8 | 226.8 | 219.35 | 231.4 | 207.8 | 205.6 | 221.7 | 218.6 | 210.9 | 209.1 | 227.1 | 217 | 235.8 | 236.8 | 229 | 237.4 | 236.9 | 223.825 | 237.4 | 205.6 | 220.7 | 222.9 | 228.1 | 216.8 | 224.1 | 223.9 | 224.9 | 223.1 | 225.6 | 219.3 | 221.8 | 205 | 221.35 | 228.1 | 205
2026-05-11 | 11:45:00.000 | 231.4 | 233.8 | 234.7 | 241.1 | 238.1 | 235.5 | 237.6 | 240.7 | 249.5 | 243.8 | 243.1 | 244.7 | 239.5 | 249.5 | 231.4 | 231 | 233.9 | 236.6 | 229.9 | 229.7 | 250.7 | 248 | 253.3 | 254 | 247.8 | 257.9 | 259.6 | 244.3667 | 259.6 | 229.7 | 246.3 | 242.6 | 246.2 | 238.7 | 248.8 | 220.4 | 250.5 | 243.7 | 243.4 | 239.9 | 245.7 | 221.3 | 240.625 | 250.5 | 220.4
2026-05-11 | 12:00:00.000 | 235.9 | 240.9 | 241.5 | 248.4 | 243.9 | 238.7 | 244.9 | 261.2 | 259.1 | 255.7 | 256.9 | 253.7 | 248.4 | 261.2 | 235.9 | 241 | 253.1 | 245.5 | 241.6 | 230 | 260.9 | 260.4 | 264.4 | 255.6 | 255.1 | 267.1 | 269.5 | 253.6833 | 269.5 | 230 | 264.3 | 252.8 | 260.5 | 258.2 | 251.4 | 249.1 | 241 | 253 | 253.2 | 253.5 | 255.3 | 232.5 | 252.0667 | 264.3 | 232.5
2026-05-11 | 12:15:00.000 | 242.5 | 244.2 | 244.6 | 250.1 | 241.1 | 236.9 | 249.9 | 263.1 | 263.7 | 257 | 263.2 | 258.6 | 251.2417 | 263.7 | 236.9 | 242.6 | 244.4 | 239.8 | 241.4 | 240 | 263.5 | 261 | 270.1 | 254.6 | 260.1 | 272.5 | 273.5 | 255.2917 | 273.5 | 239.8 | 273.3 | 256.7 | 260 | 259.3 | 261.6 | 257.2 | 263.1 | 246.3 | 246.5 | 250 | 259.3 | 222.9 | 254.6833 | 273.3 | 222.9
2026-05-11 | 12:30:00.000 | 219.5 | 216.3 | 217.1 | 226.1 | 222.2 | 215.2 | 223.9 | 228.3 | 235.2 | 235.4 | 236.8 | 231.2 | 225.6 | 236.8 | 215.2 | 221.4 | 229.2 | 223.8 | 212.9 | 218.7 | 238.1 | 236.4 | 244.6 | 241.6 | 231.9 | 249.8 | 250.6 | 233.25 | 250.6 | 212.9 | 256.5 | 235.1 | 236.5 | 230.9 | 220.7 | 232.8 | 241.6 | 230 | 222.6 | 229.5 | 234.4 | 213.1 | 231.975 | 256.5 | 213.1
2026-05-11 | 12:45:00.000 | 248.7 | 250.6 | 252.7 | 257.5 | 257.3 | 252.6 | 255.7 | 270.5 | 269.5 | 266.7 | 271.9 | 263.4 | 259.7583 | 271.9 | 248.7 | 250.3 | 260.3 | 255.8 | 247.6 | 246.2 | 271.9 | 266.7 | 277.2 | 278.4 | 267 | 279.9 | 280.3 | 265.1333 | 280.3 | 246.2 | 281.3 | 268.7 | 269.7 | 257.9 | 270.3 | 266.4 | 272.2 | 264.7 | 265.4 | 260.6 | 266.5 | 240.3 | 265.3333 | 281.3 | 240.3
2026-05-11 | 13:00:00.000 | 241.8 | 243.9 | 244.6 | 250.6 | 250.8 | 245.2 | 248.7 | 262.9 | 263.1 | 258 | 263.7 | 256.3 | 252.4667 | 263.7 | 241.8 | 236.5 | 252.8 | 240.3 | 241.1 | 239.4 | 264 | 258.2 | 270.8 | 271.4 | 259.2 | 272.7 | 273.5 | 256.6583 | 273.5 | 236.5 | 271.2 | 266.9 | 260.5 | 259 | 262.6 | 257.7 | 264.2 | 256.2 | 257.1 | 253.6 | 259.6 | 225.3 | 257.825 | 271.2 | 225.3
2026-05-11 | 13:15:00.000 | 236.2 | 238.1 | 238.5 | 244.2 | 244 | 238.6 | 243.9 | 256.3 | 247.1 | 244.1 | 256.2 | 240.3 | 243.9583 | 256.3 | 236.2 | 239.1 | 246.2 | 243 | 225.6 | 231.7 | 256.8 | 252.7 | 265.8 | 267.3 | 255.1 | 266.5 | 268.3 | 251.5083 | 268.3 | 225.6 | 278.1 | 268.1 | 254.8 | 243.8 | 256 | 243.8 | 258.7 | 252.1 | 250.9 | 244.8 | 253.2 | 228.4 | 252.725 | 278.1 | 228.4
2026-05-11 | 13:30:00.000 | 242.8 | 245.1 | 245.9 | 250.5 | 252 | 245 | 248.5 | 264.3 | 264.3 | 261.2 | 266.3 | 257.9 | 253.65 | 266.3 | 242.8 | 245.9 | 255.6 | 249.2 | 242.2 | 242.1 | 267.2 | 260.5 | 272.4 | 274.3 | 262.2 | 276.1 | 278.1 | 260.4833 | 278.1 | 242.1 | 281.2 | 269.8 | 245.7 | 261.8 | 264.5 | 261.3 | 257.2 | 258.1 | 258.9 | 256.2 | 260.5 | 236.3 | 259.2917 | 281.2 | 236.3
2026-05-11 | 13:45:00.000 | 239.6 | 241.4 | 243.8 | 247 | 247.9 | 235.3 | 245.5 | 260.3 | 259.8 | 256.8 | 261.8 | 253.6 | 249.4 | 261.8 | 235.3 | 242.4 | 250.9 | 246.7 | 228.9 | 237.9 | 262.3 | 255.6 | 259.2 | 269.2 | 257.3 | 271.9 | 273.3 | 254.6333 | 273.3 | 228.9 | 279.9 | 277.6 | 258.9 | 256.9 | 259.8 | 256.1 | 262.1 | 254.1 | 256.4 | 251.8 | 256.3 | 218.5 | 257.3667 | 279.9 | 218.5
2026-05-11 | 14:00:00.000 | 241.2 | 243.4 | 244.5 | 249.4 | 249.2 | 244.6 | 248 | 262.5 | 262.3 | 258.8 | 263.5 | 256.6 | 252 | 263.5 | 241.2 | 244.1 | 253.5 | 248.1 | 239.5 | 239.6 | 265 | 250.1 | 270.3 | 272.1 | 260.2 | 275.1 | 276.7 | 257.8583 | 276.7 | 239.5 | 281 | 281.3 | 259 | 259.2 | 262.7 | 258 | 264.7 | 256 | 257.9 | 244.4 | 259 | 234.9 | 259.8417 | 281.3 | 234.9
2026-05-11 | 14:15:00.000 | 242.6 | 244.8 | 245.5 | 250.8 | 250.8 | 246 | 249.3 | 264.2 | 264.1 | 260.7 | 265.1 | 257.8 | 253.475 | 265.1 | 242.6 | 246 | 255.3 | 241.4 | 240.9 | 240.4 | 266.7 | 260.8 | 272 | 273.7 | 261.2 | 275.8 | 277.6 | 259.3167 | 277.6 | 240.4 | 271 | 281.3 | 248.3 | 260.4 | 264.4 | 259.5 | 266.6 | 257.4 | 259.5 | 255.7 | 262 | 236.1 | 260.1833 | 281.3 | 236.1
2026-05-11 | 14:30:00.000 | 242.6 | 236.2 | 245.8 | 250.9 | 250.9 | 246.4 | 249.5 | 264.7 | 264.6 | 260.6 | 265.6 | 257.5 | 252.9417 | 265.6 | 236.2 | 246.3 | 246.8 | 249.9 | 241 | 240.5 | 266.8 | 260.6 | 272 | 273.6 | 261 | 275.5 | 277.2 | 259.2667 | 277.2 | 240.5 | 281 | 281.2 | 255.5 | 260.6 | 264.5 | 260.2 | 266.8 | 258 | 260.1 | 256.8 | 265 | 236.9 | 262.2167 | 281.2 | 236.9
2026-05-11 | 14:45:00.000 | 242.9 | 244.9 | 245.7 | 251.2 | 251.1 | 246.3 | 249.6 | 264.1 | 264.5 | 252.3 | 266 | 248.8 | 252.2833 | 266 | 242.9 | 246.8 | 256.1 | 250.1 | 241.1 | 240.1 | 267.4 | 252.3 | 272.5 | 273.5 | 261.3 | 275.1 | 267.5 | 258.65 | 275.1 | 240.1 | 280.1 | 281.3 | 262.4 | 251 | 255.2 | 260.1 | 267.5 | 249.6 | 260.2 | 257 | 256.8 | 237 | 259.85 | 281.3 | 237
2026-05-11 | 15:00:00.000 | 242 | 244.1 | 245 | 250.2 | 250 | 245.7 | 249 | 263.9 | 264.4 | 260.5 | 265.4 | 256.9 | 253.0917 | 265.4 | 242 | 245.8 | 255.2 | 249.2 | 240.3 | 239.3 | 266.7 | 261 | 272.2 | 274 | 261.4 | 275.8 | 277.5 | 259.8667 | 277.5 | 239.3 | 281 | 281.3 | 261 | 247.9 | 263.9 | 260.1 | 266.9 | 257.4 | 259.6 | 256.3 | 260.4 | 236.2 | 261 | 281.3 | 236.2
2026-05-11 | 15:15:00.000 | 241.4 | 243.4 | 244.3 | 249.6 | 249.8 | 228 | 248.6 | 262.9 | 263.3 | 259.7 | 255.3 | 255.9 | 250.1833 | 263.3 | 228 | 245.2 | 254.5 | 248.6 | 239.5 | 238.6 | 265.6 | 259.7 | 271.3 | 273 | 251.3 | 275 | 276.8 | 258.2583 | 276.8 | 238.6 | 281 | 281.3 | 258.7 | 245.9 | 262.4 | 258.7 | 266.2 | 256.5 | 258.7 | 255.3 | 258 | 227.6 | 259.1917 | 281.3 | 227.6
2026-05-11 | 15:30:00.000 | 240.6 | 242.6 | 243.4 | 248.7 | 248.8 | 244.4 | 247.7 | 262.2 | 262.6 | 258.9 | 263.8 | 255.4 | 251.5917 | 263.8 | 240.6 | 244.2 | 253.6 | 247.8 | 238.8 | 229.8 | 264.9 | 259 | 261 | 272.5 | 260.2 | 274.6 | 276.6 | 256.9167 | 276.6 | 229.8 | 281 | 281.3 | 257.6 | 243.9 | 261.9 | 249.3 | 265.6 | 255.8 | 241 | 254.7 | 245.9 | 234.9 | 256.075 | 281.3 | 234.9
2026-05-11 | 15:45:00.000 | 240.7 | 242.9 | 243.8 | 249 | 249.4 | 244.8 | 248.3 | 262.5 | 263 | 250.6 | 264.3 | 256.1 | 251.2833 | 264.3 | 240.7 | 236 | 253.9 | 248.2 | 239.2 | 238.4 | 264.9 | 259 | 270.7 | 272.6 | 260.3 | 275 | 277 | 257.9333 | 277 | 236 | 281 | 281.3 | 258.3 | 240.1 | 262.2 | 258.6 | 266.1 | 256.1 | 248.1 | 255.6 | 253.1 | 235.7 | 258.0167 | 281.3 | 235.7
2026-05-11 | 16:00:00.000 | 239.6 | 241.8 | 242.9 | 247.5 | 248 | 243.5 | 247 | 261.4 | 262.2 | 258.3 | 263.5 | 255.3 | 250.9167 | 263.5 | 239.6 | 243.1 | 252.7 | 247.1 | 238.1 | 237.6 | 264.3 | 258.3 | 270.1 | 272.2 | 259.8 | 274.7 | 276.9 | 257.9083 | 276.9 | 237.6 | 281 | 281.3 | 263 | 261.8 | 258.2 | 257.7 | 255.7 | 254.9 | 254.6 | 245 | 277.3 | 235.1 | 260.4667 | 281.3 | 235.1
2026-05-11 | 16:15:00.000 | 237.6 | 240 | 240.9 | 245.5 | 245.8 | 241.3 | 245 | 259.1 | 260 | 256.4 | 261.4 | 253.6 | 248.8833 | 261.4 | 237.6 | 240.7 | 250.3 | 244.8 | 235.9 | 235.7 | 261.9 | 256.3 | 257.9 | 270.1 | 248.7 | 273 | 275.1 | 254.2 | 275.1 | 235.7 | 281 | 281.3 | 261.1 | 245.2 | 217.5 | 255.6 | 262.8 | 252.8 | 253.9 | 207 | 281 | 216.6 | 251.3167 | 281.3 | 207
2026-05-11 | 16:30:00.000 | 234.8 | 237.3 | 238.7 | 234.7 | 243.8 | 239.3 | 242.8 | 256.8 | 257.5 | 253.9 | 259 | 251.2 | 245.8167 | 259 | 234.7 | 237.5 | 239.2 | 242.1 | 233.8 | 233.8 | 259.4 | 254.3 | 265.5 | 268.5 | 256.3 | 271.4 | 264.3 | 252.175 | 271.4 | 233.8 | 281.3 | 281.2 | 258.4 | 247.3 | 207.3 | 235.4 | 260.3 | 250.3 | 250.5 | 196.3 | 278.7 | 230.6 | 248.1333 | 281.3 | 196.3
2026-05-11 | 16:45:00.000 | 231.8 | 234.3 | 235.2 | 239.5 | 240.2 | 235.8 | 239 | 244.2 | 253.5 | 250.1 | 255.1 | 247.8 | 242.2083 | 255.1 | 231.8 | 234.1 | 243.3 | 238.5 | 230.2 | 230.7 | 255.6 | 250.3 | 261.5 | 264.1 | 252.3 | 267.5 | 269.9 | 249.8333 | 269.9 | 230.2 | 281.2 | 280.4 | 254.8 | 250.3 | 224.1 | 249.7 | 248 | 246.6 | 249.4 | 215.5 | 274.9 | 219.6 | 249.5417 | 281.2 | 215.5
2026-05-11 | 17:00:00.000 | 227 | 229.6 | 230.5 | 234.5 | 227.2 | 230.3 | 233.4 | 247.5 | 248.2 | 245.5 | 250 | 243.2 | 237.2417 | 250 | 227 | 228.6 | 237.3 | 232.9 | 225.4 | 226.4 | 250.3 | 245.1 | 256 | 259.4 | 247.9 | 263 | 265 | 244.775 | 265 | 225.4 | 280.9 | 274.7 | 249.5 | 250.8 | 256.1 | 235.9 | 251.5 | 241.8 | 246.7 | 252.6 | 269.7 | 223.9 | 252.8417 | 280.9 | 223.9
2026-05-11 | 17:15:00.000 | 180.5 | 181.7 | 187.7 | 185.2 | 190.4 | 186.5 | 185.7 | 202.5 | 201.1 | 197.1 | 203.5 | 191.4 | 191.1083 | 203.5 | 180.5 | 183.6 | 187 | 187.1 | 178.3 | 179.4 | 196.8 | 194.2 | 204.5 | 207.8 | 197.4 | 201.2 | 209.6 | 193.9083 | 209.6 | 178.3 | 223.3 | 221.9 | 197.7 | 208.6 | 204.9 | 196.5 | 203.7 | 197.9 | 201 | 202.2 | 220.1 | 182.6 | 205.0333 | 223.3 | 182.6
2026-05-11 | 17:30:00.000 | 193.8 | 196.4 | 195.9 | 199.8 | 200.3 | 195.6 | 203 | 215.4 | 216.4 | 213.8 | 216.9 | 205.3 | 204.3833 | 216.9 | 193.8 | 193 | 200.9 | 190.2 | 189.4 | 190.9 | 209.9 | 204.4 | 212.4 | 215.8 | 204.4 | 215.2 | 215.5 | 203.5 | 215.8 | 189.4 | 256 | 248.2 | 222.2 | 234.1 | 227.5 | 216.6 | 223.3 | 213 | 218.1 | 225.8 | 242.1 | 196 | 226.9083 | 256 | 196
2026-05-11 | 17:45:00.000 | 172 | 174.6 | 174.1 | 177 | 177.8 | 173.1 | 177 | 192.3 | 186.9 | 191 | 195 | 183.1 | 181.1583 | 195 | 172 | 169.9 | 177.2 | 173.5 | 166.4 | 167.4 | 184.6 | 181.9 | 188.1 | 191.5 | 181.1 | 189.8 | 191.1 | 180.2083 | 191.5 | 166.4 | 232.8 | 226.2 | 201.4 | 209.8 | 202.5 | 192.4 | 199.6 | 190.7 | 196.3 | 205.2 | 217.6 | 174.6 | 204.0917 | 232.8 | 174.6
2026-05-11 | 18:00:00.000 | 139.1 | 141.2 | 141.2 | 143.7 | 144.8 | 140.8 | 140.5 | 157.1 | 157.4 | 156.2 | 160 | 149 | 147.5833 | 160 | 139.1 | 140 | 144.9 | 142.4 | 135.1 | 136.7 | 151.4 | 149 | 153.1 | 155.3 | 146.7 | 153.3 | 155 | 146.9083 | 155.3 | 135.1 | 187.2 | 181.5 | 164.9 | 170.9 | 165.9 | 157.5 | 158.7 | 157.1 | 157.2 | 169.9 | 179.2 | 143.7 | 166.1417 | 187.2 | 143.7
2026-05-11 | 18:15:00.000 | 107.7 | 109.8 | 110.8 | 111.5 | 112.6 | 109.2 | 107.4 | 124.2 | 124.1 | 121.4 | 125.5 | 116.3 | 115.0417 | 125.5 | 107.4 | 107.3 | 111.7 | 109.1 | 104.9 | 106 | 116.5 | 116.3 | 118.9 | 121.1 | 114.6 | 120 | 121.2 | 113.9667 | 121.2 | 104.9 | 154 | 147.2 | 129 | 131.4 | 127.4 | 121.6 | 126.3 | 122.8 | 127 | 134.7 | 139.8 | 112.6 | 131.15 | 154 | 112.6
2026-05-11 | 18:30:00.000 | 67.6 | 68.5 | 68.5 | 69.4 | 70.4 | 67.7 | 66.4 | 77.1 | 77.4 | 73.9 | 78.4 | 73.8 | 71.5917 | 78.4 | 66.4 | 67 | 69.5 | 67.9 | 65.4 | 65.7 | 72.9 | 72.8 | 75 | 76 | 71.4 | 74.6 | 72.8 | 70.9167 | 76 | 65.4 | 96.9 | 93.6 | 80.5 | 82.9 | 77.7 | 76.8 | 80.2 | 77.7 | 79.7 | 83.8 | 88.3 | 70 | 82.3417 | 96.9 | 70
2026-05-11 | 18:45:00.000 | 66.5 | 67.5 | 67.3 | 68.6 | 69.3 | 66.1 | 64.4 | 76.8 | 77.1 | 75.9 | 77.9 | 71.9 | 70.775 | 77.9 | 64.4 | 66 | 68.3 | 67.2 | 63.4 | 63.8 | 70.8 | 70.3 | 72.5 | 72.6 | 67.8 | 70.4 | 71 | 68.675 | 72.6 | 63.4 | 92.9 | 93.6 | 79.6 | 81.5 | 79.5 | 76.1 | 79.6 | 76.7 | 79.3 | 84.3 | 86.9 | 69.9 | 81.6583 | 93.6 | 69.9
2026-05-11 | 19:00:00.000 | 44.3 | 44.8 | 44.4 | 45.5 | 46.1 | 43.4 | 43.3 | 51.4 | 51.5 | 50.6 | 51.8 | 48 | 47.0917 | 51.8 | 43.3 | 43.6 | 45.1 | 44.5 | 41.4 | 41.9 | 46.2 | 46 | 47.6 | 47.3 | 43.8 | 44.9 | 45.5 | 44.8167 | 47.6 | 41.4 | 64.5 | 63.1 | 53.1 | 54.4 | 52.7 | 50.6 | 53.3 | 49.5 | 53.5 | 57.1 | 58.4 | 47 | 54.7667 | 64.5 | 47
2026-05-11 | 19:15:00.000 | 24.7 | 24.9 | 24.5 | 25.4 | 25.6 | 24.3 | 25 | 29.1 | 29.1 | 28.5 | 29 | 27.2 | 26.4417 | 29.1 | 24.3 | 24.5 | 25.6 | 25 | 23.1 | 23.5 | 25.8 | 25.7 | 26.6 | 26.3 | 24.2 | 24.7 | 25.1 | 25.0083 | 26.6 | 23.1 | 37.2 | 36.1 | 30.4 | 31.1 | 30.1 | 28.7 | 30.3 | 29.2 | 30.7 | 33 | 33.4 | 26.8 | 31.4167 | 37.2 | 26.8
2026-05-11 | 19:30:00.000 | 17.2 | 17.3 | 17 | 17.9 | 17.9 | 17.1 | 18.1 | 21 | 21 | 20.4 | 20.7 | 19.5 | 18.7583 | 21 | 17 | 17 | 18.1 | 17.5 | 15.9 | 16.3 | 18 | 17.9 | 18.6 | 18.4 | 17 | 17.4 | 17.8 | 17.4917 | 18.6 | 15.9 | 26.4 | 26.3 | 22.3 | 22.7 | 22 | 20.3 | 21.7 | 20.9 | 22.2 | 24.3 | 23.6 | 19.4 | 22.675 | 26.4 | 19.4
2026-05-11 | 19:45:00.000 | 10.6 | 10.6 | 10.4 | 10.8 | 10.9 | 10.5 | 11.1 | 12.4 | 12.4 | 12.1 | 12.2 | 11.8 | 11.3167 | 12.4 | 10.4 | 10.7 | 11.2 | 10.9 | 10.3 | 10.6 | 11.8 | 12.3 | 13.1 | 13.4 | 13.3 | 14.2 | 14.6 | 12.2 | 14.6 | 10.3 | 15.2 | 15.4 | 13.2 | 13.5 | 13.1 | 12 | 12.7 | 12.3 | 13 | 14.2 | 13.9 | 11.4 | 13.325 | 15.4 | 11.4
2026-05-11 | 20:00:00.000 | 4.6 | 4.5 | 4.6 | 4.7 | 4.8 | 4.7 | 4.6 | 5.1 | 5.1 | 5 | 5.1 | 4.9 | 4.8083 | 5.1 | 4.5 | 4.6 | 4.8 | 4.7 | 4.5 | 4.5 | 5 | 5.1 | 5.3 | 5.4 | 5.1 | 5.4 | 5.5 | 4.9917 | 5.5 | 4.5 | 5.6 | 5.4 | 4.8 | 4.9 | 5 | 4.6 | 4.8 | 4.7 | 4.9 | 5 | 5.2 | 4.3 | 4.9333 | 5.6 | 4.3
2026-05-11 | 20:15:00.000 | 0.9 | 0.7 | 1.1 | 1.2 | 1 | 1.1 | 1.2 | 1.2 | 1.3 | 1.2 | 1.2 | 1.2 | 1.1083 | 1.3 | 0.7 | 1.1 | 1.2 | 0.9 | 1.2 | 1.2 | 1.3 | 1.3 | 1.4 | 1.4 | 1.2 | 1.2 | 1.3 | 1.225 | 1.4 | 0.9 | 1.4 | 1.3 | 1.3 | 1.3 | 1.4 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.4 | 1.1 | 1.2917 | 1.4 | 1.1
2026-05-11 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.4 | 0.20833 | 1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.1 | 0.6 | 0.1 | 0.2 | 0.7 | 0.3 | 0.2 | 0.1 | 0.9 | 0.325 | 0.9 | 0.1 | 0.7 | 0.4 | 0.2 | 0.1 | 0.2 | 0.2 | 0.1 | 0.2 | 0.1 | 0.2 | 0.3 | 0.1 | 0.23333 | 0.7 | 0.1
2026-05-11 | 20:45:00.000 | 0 | 0 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.17 | 0.7 | 0 | 0.1 | 0.1 | 0.7 | 0.1 | 0.3 | 0.1 | 0.1 | 0.7 | 0.1 | 0.1 | 0.1 | 0.8 | 0.275 | 0.8 | 0.1 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13333 | 0.5 | 0.1
2026-05-11 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.3 | 0.25 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0
2026-05-11 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.125 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320