## PR_Calc
PR CALCULATION
13 MAGGIO 2026 | [67 empty] | 13 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 51
RAW PR | [64 empty] | 0.76013 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 76.0133
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 75.9787
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 76.0133
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-13 | 00:00:00.000 | -2 | -0.0005 | -1.9 | -0.000475 | -0.0004875 | 0 | -0.0004875 | 0 | 30901.6 | 30979.9 | 78300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9256.4
2026-05-13 | 00:15:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 00:30:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 00:45:00.000 | -1 | -0.00025 | -0.2 | -5e-05 | -0.00015 | 0 | -0.00015 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 01:00:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 01:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 01:30:00.000 | -0.3 | -7.5e-05 | -0.5 | -0.000125 | -0.0001 | 0 | -0.0001 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 02:15:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 03:00:00.000 | -0.7 | -0.000175 | -0.6 | -0.00015 | -0.0001625 | 0 | -0.0001625 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 03:15:00.000 | -1.4 | -0.00035 | -1 | -0.00025 | -0.0003 | 0 | -0.0003 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 03:30:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 03:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 04:00:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 04:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 04:30:00.000 | -1.8 | -0.00045 | -1.2 | -0.0003 | -0.000375 | 0 | -0.000375 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 04:45:00.000 | -0.9 | -0.000225 | -1.1 | -0.000275 | -0.00025 | 0 | -0.00025 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 05:00:00.000 | -1 | -0.00025 | -0.7 | -0.000175 | -0.0002125 | 0 | -0.0002125 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 05:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 05:30:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 05:45:00.000 | -0.4 | -0.0001 | -0.2 | -5e-05 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 06:00:00.000 | 2.8 | 0.0007 | 2.8 | 0.0007 | 0.0007 | 0 | 0.0007 | 0 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 06:15:00.000 | 8 | 0.002 | 8.4 | 0.0021 | 0.00205 | 0 | 0.00205 | 0.04878 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 06:30:00.000 | 22.2 | 0.00555 | 22.4 | 0.0056 | 0.005575 | 0 | 0.005575 | 0.0089686 | 30979.9 | 30979.9 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 06:45:00.000 | 42.9 | 0.010725 | 43.6 | 0.0109 | 0.010812 | 0 | 0.010812 | 0.016185 | 30979.9 | 30980 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 07:00:00.000 | 85.1 | 0.021275 | 87.4 | 0.02185 | 0.021562 | 86.25 | 0.02185 | 0.026667 | 30980 | 30980.1 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 07:15:00.000 | 145.5 | 0.036375 | 144.4 | 0.0361 | 0.036237 | 144.95 | 0.036375 | 0.0075888 | 30980.1 | 30980.4 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 07:30:00.000 | 192.1 | 0.048025 | 191.6 | 0.0479 | 0.047962 | 191.85 | 0.048025 | 0.0026062 | 30980.4 | 30980.8 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 07:45:00.000 | 379.7 | 0.094925 | 390.8 | 0.0977 | 0.096312 | 385.25 | 0.0977 | 0.028812 | 30980.8 | 30981.6 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 08:00:00.000 | 373.8 | 0.09345 | 390.6 | 0.09765 | 0.09555 | 382.2 | 0.09765 | 0.043956 | 30981.6 | 30982.6 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 08:15:00.000 | 425.4 | 0.10635 | 431.3 | 0.10783 | 0.10709 | 428.35 | 0.10783 | 0.013774 | 30982.6 | 30983.5 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 08:30:00.000 | 663.4 | 0.16585 | 651.9 | 0.16297 | 0.16441 | 657.65 | 0.16585 | 0.017487 | 30983.5 | 30984.9 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 08:45:00.000 | 810.6 | 0.20265 | 795.9 | 0.19897 | 0.20081 | 803.25 | 0.20265 | 0.018301 | 30984.9 | 30986.8 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 09:00:00.000 | 886.6 | 0.22165 | 880.1 | 0.22002 | 0.22084 | 883.35 | 0.22165 | 0.0073584 | 30986.8 | 30988.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 09:15:00.000 | 906 | 0.2265 | 899.3 | 0.22482 | 0.22566 | 902.65 | 0.2265 | 0.0074226 | 30988.9 | 30991.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 09:30:00.000 | 934.7 | 0.23368 | 923.8 | 0.23095 | 0.23231 | 929.25 | 0.23368 | 0.01173 | 30991.2 | 30993.5 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 09:45:00.000 | 943.9 | 0.23597 | 939.2 | 0.2348 | 0.23539 | 941.55 | 0.23597 | 0.0049918 | 30993.5 | 30995.8 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 10:00:00.000 | 955.4 | 0.23885 | 940.6 | 0.23515 | 0.237 | 948 | 0.23885 | 0.015612 | 30995.8 | 30998.1 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 10:15:00.000 | 965.9 | 0.24147 | 950.9 | 0.23772 | 0.2396 | 958.4 | 0.24147 | 0.015651 | 30998.1 | 31000.4 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 10:30:00.000 | 957.4 | 0.23935 | 947.5 | 0.23688 | 0.23811 | 952.45 | 0.23935 | 0.010394 | 31000.4 | 31002.8 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 10:45:00.000 | 990.1 | 0.24752 | 957.4 | 0.23935 | 0.24344 | 973.75 | 0.24752 | 0.033582 | 31002.8 | 31005.2 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 11:00:00.000 | 742.9 | 0.18573 | 673.7 | 0.16843 | 0.17708 | 708.3 | 0.18573 | 0.097699 | 31005.2 | 31007 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 11:15:00.000 | 974 | 0.2435 | 951.9 | 0.23797 | 0.24074 | 962.95 | 0.2435 | 0.02295 | 31007 | 31009 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 11:30:00.000 | 982.6 | 0.24565 | 909.3 | 0.22732 | 0.23649 | 945.95 | 0.24565 | 0.077488 | 31009 | 31011.3 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 11:45:00.000 | 1020.8 | 0.2552 | 997.4 | 0.24935 | 0.25227 | 1009.1 | 0.2552 | 0.023189 | 31011.3 | 31013.7 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 12:00:00.000 | 1010.7 | 0.25268 | 979.6 | 0.2449 | 0.24879 | 995.15 | 0.25268 | 0.031252 | 31013.7 | 31016.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 12:15:00.000 | 1042.3 | 0.26058 | 998.9 | 0.24973 | 0.25515 | 1020.6 | 0.26058 | 0.042524 | 31016.1 | 31018.5 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 12:30:00.000 | 822.9 | 0.20572 | 770.2 | 0.19255 | 0.19914 | 796.55 | 0.20572 | 0.06616 | 31018.5 | 31020.7 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 12:45:00.000 | 837 | 0.20925 | 800.5 | 0.20012 | 0.20469 | 818.75 | 0.20925 | 0.04458 | 31020.7 | 31022.7 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 13:00:00.000 | 774.6 | 0.19365 | 784.5 | 0.19612 | 0.19489 | 779.55 | 0.19612 | 0.0127 | 31022.7 | 31024.3 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 13:15:00.000 | 753.2 | 0.1883 | 830.4 | 0.2076 | 0.19795 | 791.8 | 0.2076 | 0.097499 | 31024.3 | 31026.1 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 13:30:00.000 | 846.1 | 0.21153 | 756.9 | 0.18923 | 0.20038 | 801.5 | 0.21153 | 0.11129 | 31026.1 | 31027.9 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 13:45:00.000 | 806 | 0.2015 | 841.3 | 0.21032 | 0.20591 | 823.65 | 0.21032 | 0.042858 | 31027.9 | 31029.7 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 14:00:00.000 | 959.3 | 0.23982 | 920 | 0.23 | 0.23491 | 939.65 | 0.23982 | 0.041824 | 31029.7 | 31031.6 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 14:15:00.000 | 1046.6 | 0.26165 | 941.4 | 0.23535 | 0.2485 | 994 | 0.26165 | 0.10584 | 31031.6 | 31033.9 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 14:30:00.000 | 876.9 | 0.21923 | 857.9 | 0.21447 | 0.21685 | 867.4 | 0.21923 | 0.021905 | 31033.9 | 31035.9 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 14:45:00.000 | 960.9 | 0.24022 | 934.7 | 0.23368 | 0.23695 | 947.8 | 0.24022 | 0.027643 | 31035.9 | 31038.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 15:00:00.000 | 984.6 | 0.24615 | 925.2 | 0.2313 | 0.23873 | 954.9 | 0.24615 | 0.062205 | 31038.2 | 31040.3 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 15:15:00.000 | 963.2 | 0.2408 | 903.8 | 0.22595 | 0.23337 | 933.5 | 0.2408 | 0.063631 | 31040.3 | 31042.6 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 15:30:00.000 | 1005.9 | 0.25148 | 973.6 | 0.2434 | 0.24744 | 989.75 | 0.25148 | 0.032635 | 31042.6 | 31044.8 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 15:45:00.000 | 1005.2 | 0.2513 | 980.2 | 0.24505 | 0.24818 | 992.7 | 0.2513 | 0.025184 | 31044.8 | 31047.2 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 16:00:00.000 | 1012.9 | 0.25322 | 987.3 | 0.24682 | 0.25002 | 1000.1 | 0.25322 | 0.025597 | 31047.2 | 31049.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 16:15:00.000 | 911.7 | 0.22793 | 980.1 | 0.24502 | 0.23647 | 945.9 | 0.24502 | 0.072312 | 31049.6 | 31052 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 16:30:00.000 | 700.2 | 0.17505 | 952 | 0.238 | 0.20653 | 826.1 | 0.238 | 0.30481 | 31052 | 31054 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 16:45:00.000 | 659.9 | 0.16497 | 952.4 | 0.2381 | 0.20154 | 806.15 | 0.2381 | 0.36284 | 31054 | 31056 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 17:00:00.000 | 606.7 | 0.15168 | 932 | 0.233 | 0.19234 | 769.35 | 0.233 | 0.42282 | 31056 | 31057.8 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 17:15:00.000 | 577.3 | 0.14432 | 940.6 | 0.23515 | 0.18974 | 758.95 | 0.23515 | 0.47869 | 31057.8 | 31059.6 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 17:30:00.000 | 559.1 | 0.13978 | 729 | 0.18225 | 0.16101 | 644.05 | 0.18225 | 0.2638 | 31059.6 | 31061.2 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 17:45:00.000 | 708.3 | 0.17707 | 742.7 | 0.18568 | 0.18138 | 725.5 | 0.18568 | 0.047416 | 31061.2 | 31062.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 18:00:00.000 | 621.3 | 0.15532 | 700.9 | 0.17522 | 0.16528 | 661.1 | 0.17522 | 0.12041 | 31062.7 | 31064.3 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 18:15:00.000 | 493 | 0.12325 | 540.9 | 0.13522 | 0.12924 | 516.95 | 0.13522 | 0.092659 | 31064.3 | 31065.6 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 18:30:00.000 | 382.6 | 0.09565 | 428.3 | 0.10708 | 0.10136 | 405.45 | 0.10708 | 0.11271 | 31065.6 | 31066.7 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 18:45:00.000 | 262.3 | 0.065575 | 319.2 | 0.0798 | 0.072688 | 290.75 | 0.0798 | 0.1957 | 31066.7 | 31067.5 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 19:00:00.000 | 173.2 | 0.0433 | 218.7 | 0.054675 | 0.048987 | 195.95 | 0.054675 | 0.2322 | 31067.5 | 31067.9 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 19:15:00.000 | 136.9 | 0.034225 | 150.3 | 0.037575 | 0.0359 | 143.6 | 0.037575 | 0.093315 | 31067.9 | 31068.3 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 19:30:00.000 | 95.1 | 0.023775 | 99.8 | 0.02495 | 0.024362 | 97.45 | 0.02495 | 0.04823 | 31068.3 | 31068.5 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 19:45:00.000 | 37.8 | 0.00945 | 60.7 | 0.015175 | 0.012313 | 0 | 0.012313 | 0.46497 | 31068.5 | 31068.7 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 20:00:00.000 | 17.6 | 0.0044 | 17.6 | 0.0044 | 0.0044 | 0 | 0.0044 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 20:15:00.000 | 4.2 | 0.00105 | 4.2 | 0.00105 | 0.00105 | 0 | 0.00105 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 20:30:00.000 | -0.3 | -7.5e-05 | -0.5 | -0.000125 | -0.0001 | 0 | -0.0001 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 20:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 21:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 21:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 21:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 21:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 22:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 22:15:00.000 | -1 | -0.00025 | -1.4 | -0.00035 | -0.0003 | 0 | -0.0003 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 22:30:00.000 | -1 | -0.00025 | -1.2 | -0.0003 | -0.000275 | 0 | -0.000275 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 22:45:00.000 | -1 | -0.00025 | -1.9 | -0.000475 | -0.0003625 | 0 | -0.0003625 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 23:00:00.000 | -1 | -0.00025 | -1.9 | -0.000475 | -0.0003625 | 0 | -0.0003625 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 23:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 23:30:00.000 | -1 | -0.00025 | -1.1 | -0.000275 | -0.0002625 | 0 | -0.0002625 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
2026-05-13 | 23:45:00.000 | -1 | -0.00025 | -1.6 | -0.0004 | -0.000325 | 0 | -0.000325 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88362
PR for each inverter |  |  | 9.2584 |  | 9.5139 | 9.3861 |  | 9.751 |  |  |  | 167100 |  | 0.71941 | 0.73337 | 0.73233 | 0.74334 | 0.74291 | 0.73206 | 0.73963 | 0.79444 | 0.78821 | 0.75763 | 0.74994 | 0.78084 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.7521 | 0.74239 | 0.73037 | 0.73573 | 0.73447 | 0.73044 | 0.75744 | 0.74172 | 0.7444 | 0.7684 | 0.74909 | 0.76095 |  |  |  | 0 | 0.8103 | 0.7976 | 0.7707 | 0.80136 | 0.79206 | 0.75731 | 0.76448 | 0.75418 | 0.75698 | 0.80766 | 0.80336 | 0.77472 | #DIV/0! | #DIV/0! | #DIV/0! | 0 |  | 0.75979 |  | #DIV/0! | #DIV/0! | 6.0825e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-13 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0.4 | 0.3 | 0.39091 | 0.4 | 0
2026-05-13 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 1.25 | 1.8 | 0 | 2.1 | 2.2 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 1.9 | 2.125 | 2.3 | 1.9
2026-05-13 | 06:30:00.000 | 3.5 | 3.5 | 3.7 | 3.6 | 5.2 | 3.6 | 3.8 | 5.2 | 4.7 | 4.2 | 3.8 | 4.3 | 4.0917 | 5.2 | 3.5 | 4 | 4 | 5.3 | 3.8 | 4.8 | 4 | 4.4 | 5.4 | 4.4 | 4.4 | 4.1 | 5.1 | 4.475 | 5.4 | 3.8 | 6.7 | 6.6 | 6.3 | 6.7 | 6.6 | 6.3 | 6.4 | 6.2 | 6.3 | 6.6 | 6.8 | 5.8 | 6.4417 | 6.8 | 5.8
2026-05-13 | 06:45:00.000 | 3.7 | 4.1 | 2.9 | 11.1 | 0 | 10.8 | 10.9 | 12.2 | 12.3 | 11.8 | 11.5 | 11.2 | 9.3182 | 12.3 | 0 | 10.7 | 10.7 | 11.6 | 10.3 | 10.9 | 11.3 | 11.1 | 12.2 | 11.9 | 11.3 | 11.6 | 12.9 | 11.375 | 12.9 | 10.3 | 13.4 | 12.9 | 12.3 | 13.2 | 13 | 12.5 | 12.6 | 12.2 | 12.3 | 13 | 13.4 | 11.3 | 12.675 | 13.4 | 11.3
2026-05-13 | 07:00:00.000 | 20.3 | 19.7 | 22.9 | 23.1 | 7.6 | 22.5 | 22.5 | 25.9 | 25.6 | 24.6 | 24.1 | 23.6 | 21.8667 | 25.9 | 7.6 | 22.2 | 22.5 | 22.7 | 22.4 | 22.3 | 24.2 | 23.9 | 24.8 | 25.2 | 23.9 | 25.2 | 25.4 | 23.725 | 25.4 | 22.2 | 26.6 | 24.2 | 24.2 | 26.4 | 25.9 | 25.1 | 25.1 | 24.1 | 24.1 | 25.4 | 26.5 | 22.5 | 25.0083 | 26.6 | 22.5
2026-05-13 | 07:15:00.000 | 39.1 | 38.9 | 39.7 | 39.9 | 40.1 | 39.1 | 38.8 | 44.7 | 44 | 42.7 | 42 | 40.8 | 40.8167 | 44.7 | 38.8 | 38.4 | 38.7 | 39.1 | 38.6 | 38.4 | 41.7 | 41.4 | 42.9 | 43.8 | 41.3 | 43.5 | 43.7 | 40.9583 | 43.8 | 38.4 | 46.3 | 43.6 | 42.5 | 46.4 | 45.3 | 43.6 | 43.2 | 42.1 | 41.9 | 44.2 | 46 | 39 | 43.675 | 46.4 | 39
2026-05-13 | 07:30:00.000 | 52.7 | 52.5 | 53.9 | 53.7 | 53.6 | 52.8 | 53.1 | 61.3 | 60.1 | 57.3 | 56.5 | 55.2 | 55.225 | 61.3 | 52.5 | 51.8 | 52.5 | 53.2 | 51.8 | 51.4 | 56.4 | 56 | 58.1 | 59.1 | 56 | 58.8 | 58.7 | 55.3167 | 59.1 | 51.4 | 62.3 | 59.6 | 56.7 | 62 | 61 | 58.4 | 55.5 | 56.8 | 56.5 | 59.6 | 62 | 52.5 | 58.575 | 62.3 | 52.5
2026-05-13 | 07:45:00.000 | 104.9 | 103.9 | 105.6 | 106.2 | 107.2 | 104.2 | 105.7 | 121.2 | 118.2 | 114.1 | 111.4 | 108 | 109.2167 | 121.2 | 103.9 | 102.9 | 103.6 | 104.4 | 103.2 | 102.6 | 111.1 | 109.5 | 112.6 | 110 | 108.7 | 114.6 | 113.8 | 108.0833 | 114.6 | 102.6 | 121.4 | 116.8 | 110.3 | 122.8 | 120 | 113.6 | 113.5 | 106.3 | 110.1 | 118 | 121.6 | 102.5 | 114.7417 | 122.8 | 102.5
2026-05-13 | 08:00:00.000 | 101.1 | 98.8 | 100.2 | 99.8 | 101.2 | 98.2 | 98.3 | 119.8 | 116.3 | 110.1 | 105.7 | 101.8 | 104.275 | 119.8 | 98.2 | 97.5 | 98.2 | 98.7 | 94.3 | 94.2 | 105.5 | 103.6 | 108.4 | 109.3 | 103.4 | 107.2 | 107.2 | 102.2917 | 109.3 | 94.2 | 118.2 | 113.4 | 102.8 | 116.5 | 113.5 | 104.2 | 106.6 | 103.6 | 102.3 | 114.5 | 115.4 | 93.3 | 108.6917 | 118.2 | 93.3
2026-05-13 | 08:15:00.000 | 106 | 106.1 | 108.4 | 110.7 | 111 | 108.9 | 110.1 | 136.1 | 133.4 | 122.8 | 118 | 114.2 | 115.475 | 136.1 | 106 | 108.1 | 110.7 | 109.7 | 108 | 105.7 | 118.3 | 116.8 | 120.6 | 121.4 | 114.2 | 121.3 | 121.5 | 114.6917 | 121.5 | 105.7 | 132.9 | 130.2 | 113.2 | 132.7 | 122.7 | 115.2 | 118 | 113.7 | 112.8 | 131.1 | 132 | 102.3 | 121.4 | 132.9 | 102.3
2026-05-13 | 08:30:00.000 | 164.4 | 165 | 164 | 170.8 | 172.3 | 169.8 | 169.2 | 210.7 | 203.8 | 191.9 | 184.7 | 176.9 | 178.625 | 210.7 | 164 | 168.2 | 170.6 | 170.7 | 158.9 | 161.1 | 181.6 | 182.3 | 188.6 | 184.2 | 181 | 189.3 | 188.5 | 177.0833 | 189.3 | 158.9 | 209.2 | 201.4 | 183.9 | 199.8 | 202.1 | 181.3 | 185 | 176.7 | 178.5 | 206 | 202.9 | 161.8 | 190.7167 | 209.2 | 161.8
2026-05-13 | 08:45:00.000 | 202.4 | 203.8 | 207.6 | 210.8 | 210.4 | 207.5 | 210.1 | 258.6 | 251.4 | 232.2 | 224.5 | 218.1 | 219.7833 | 258.6 | 202.4 | 207 | 213.6 | 209.7 | 196.5 | 201.2 | 226.3 | 221.5 | 229.4 | 230.2 | 210 | 231.3 | 228.4 | 217.0917 | 231.3 | 196.5 | 254.2 | 245.8 | 226 | 252.1 | 245.6 | 223.8 | 225.4 | 218.5 | 221 | 252.9 | 247.3 | 201.3 | 234.4917 | 254.2 | 201.3
2026-05-13 | 09:00:00.000 | 229.7 | 230.8 | 234.1 | 238.7 | 238.6 | 235.3 | 238.3 | 281.2 | 278.7 | 262.1 | 253.2 | 245.8 | 247.2083 | 281.2 | 229.7 | 234.2 | 243.1 | 238.2 | 228.8 | 227.2 | 254.6 | 239.9 | 259.1 | 259.5 | 246.4 | 260 | 258.9 | 245.825 | 260 | 227.2 | 278.9 | 275.7 | 251.7 | 278.1 | 272.4 | 247.8 | 253.4 | 243.9 | 246.7 | 279.1 | 274.2 | 224.2 | 260.5083 | 279.1 | 224.2
2026-05-13 | 09:15:00.000 | 237 | 238.1 | 241.3 | 246.2 | 244.4 | 240.1 | 244.8 | 270.7 | 279.9 | 270.8 | 261.2 | 253.2 | 252.3083 | 279.9 | 237 | 239.2 | 239.7 | 244.9 | 233.9 | 232.3 | 263.8 | 256.5 | 267.7 | 268.9 | 255 | 268.1 | 271.7 | 253.475 | 271.7 | 232.3 | 281.4 | 281 | 259.3 | 271.7 | 278 | 254.5 | 260.4 | 249.7 | 252.6 | 280.5 | 280.9 | 230.6 | 265.05 | 281.4 | 230.6
2026-05-13 | 09:30:00.000 | 244.6 | 245.7 | 248.3 | 252.9 | 252.8 | 248.7 | 252.7 | 281.2 | 281.3 | 269.1 | 266.3 | 260.7 | 258.6917 | 281.3 | 244.6 | 247.3 | 256.9 | 251.5 | 241.9 | 240.4 | 270 | 263.4 | 275 | 275.5 | 262.4 | 276.6 | 278.9 | 261.65 | 278.9 | 240.4 | 281.5 | 281.3 | 266.8 | 281.5 | 272.2 | 262.6 | 268.2 | 257.8 | 261.1 | 281.5 | 281.3 | 238.3 | 269.5083 | 281.5 | 238.3
2026-05-13 | 09:45:00.000 | 249 | 249.5 | 251.2 | 257.1 | 252.8 | 249.1 | 256.9 | 279.9 | 281.4 | 237.7 | 214.7 | 266 | 253.775 | 281.4 | 214.7 | 251.2 | 261.1 | 256.4 | 243.9 | 245.2 | 274 | 267 | 276.1 | 275.9 | 265.2 | 279.9 | 281.5 | 264.7833 | 281.5 | 243.9 | 281.5 | 281.4 | 271.5 | 281.6 | 281.6 | 266.4 | 268.9 | 262.5 | 266 | 281.5 | 280.7 | 242.3 | 272.1583 | 281.6 | 242.3
2026-05-13 | 10:00:00.000 | 247.4 | 244.1 | 245.5 | 235.9 | 258.7 | 244.6 | 250.3 | 276.1 | 276.1 | 246.1 | 199.4 | 257.9 | 248.5083 | 276.1 | 199.4 | 249.3 | 254.2 | 253.1 | 238.5 | 237.2 | 271.4 | 268.5 | 269.1 | 269.4 | 262 | 268.3 | 273.7 | 259.5583 | 273.7 | 237.2 | 266.5 | 272.9 | 271.2 | 276.5 | 271.6 | 256.2 | 258.9 | 257.6 | 256 | 269 | 272.4 | 244.9 | 264.475 | 276.5 | 244.9
2026-05-13 | 10:15:00.000 | 252.9 | 254.3 | 255.7 | 260.9 | 260.7 | 256.3 | 260.4 | 281.2 | 281.2 | 256.9 | 213.9 | 269.9 | 258.6917 | 281.2 | 213.9 | 254.2 | 264.5 | 259.6 | 249.6 | 248.5 | 277.6 | 271.3 | 281.4 | 280.9 | 270.9 | 281.6 | 281.1 | 268.4333 | 281.6 | 248.5 | 281.1 | 281.3 | 265.8 | 281.1 | 281.1 | 270.4 | 275.6 | 266.2 | 269.5 | 281.1 | 281 | 245.1 | 273.275 | 281.3 | 245.1
2026-05-13 | 10:30:00.000 | 249.4 | 252.8 | 253.6 | 263.4 | 253.9 | 255.4 | 255.9 | 276.4 | 280.8 | 270.1 | 227.2 | 266.6 | 258.7917 | 280.8 | 227.2 | 249.5 | 249.1 | 253.2 | 242.4 | 240.5 | 276.8 | 273.5 | 280.5 | 280.5 | 270.8 | 275.8 | 278.4 | 264.25 | 280.5 | 240.5 | 280.8 | 279.1 | 274.7 | 277.7 | 278.3 | 270.9 | 274 | 267.4 | 271.7 | 280.6 | 274.6 | 243.5 | 272.775 | 280.8 | 243.5
2026-05-13 | 10:45:00.000 | 252.1 | 263.6 | 261 | 255.8 | 258.9 | 266.1 | 251.9 | 274.1 | 269.3 | 269.7 | 246.4 | 251.9 | 260.0667 | 274.1 | 246.4 | 254.3 | 268.2 | 252.4 | 255.8 | 245.7 | 263.3 | 263.1 | 264.7 | 257.1 | 260.2 | 247.8 | 256.3 | 257.4083 | 268.2 | 245.7 | 270.7 | 259.1 | 266.3 | 274.1 | 263.9 | 271.1 | 268.7 | 256.8 | 257.5 | 271.7 | 273.4 | 253.2 | 265.5417 | 274.1 | 253.2
2026-05-13 | 11:00:00.000 | 171.1 | 177.7 | 177.9 | 190.3 | 180.8 | 184.3 | 183.7 | 204.3 | 210.4 | 198.5 | 203.4 | 177.7 | 188.3417 | 210.4 | 171.1 | 191.9 | 200.4 | 193.1 | 195.7 | 185.7 | 207.3 | 208.9 | 208 | 210 | 204.3 | 210.3 | 202.9 | 201.5417 | 210.3 | 185.7 | 197 | 190.5 | 171.8 | 173.9 | 164 | 178.5 | 158.6 | 166.5 | 167.2 | 178.5 | 186.3 | 146.7 | 173.2917 | 197 | 146.7
2026-05-13 | 11:15:00.000 | 248.2 | 244.9 | 241.7 | 242.8 | 250.3 | 236.9 | 248.2 | 253.5 | 251.4 | 246.4 | 238.9 | 232.6 | 244.65 | 253.5 | 232.6 | 239.5 | 248.8 | 259.8 | 242.3 | 235.6 | 235.9 | 242.2 | 247.1 | 251.9 | 245.7 | 250.3 | 248.5 | 245.6333 | 259.8 | 235.6 | 253.8 | 259.6 | 254.2 | 247.3 | 248.4 | 244.8 | 237.4 | 248.4 | 250.8 | 255.6 | 250 | 234.9 | 248.7667 | 259.6 | 234.9
2026-05-13 | 11:30:00.000 | 256.2 | 264.1 | 259.8 | 259.2 | 265.9 | 265.6 | 265.5 | 270.6 | 264.6 | 271.9 | 264.6 | 265.2 | 264.4333 | 271.9 | 256.2 | 262.2 | 270.8 | 265.7 | 248.4 | 257.3 | 264.1 | 267.8 | 270.4 | 272.3 | 268.3 | 265.7 | 264.1 | 264.7583 | 272.3 | 248.4 | 243.4 | 240.9 | 247.1 | 258.7 | 256.2 | 253.7 | 242 | 244 | 242.9 | 225.8 | 246.6 | 219.5 | 243.4 | 258.7 | 219.5
2026-05-13 | 11:45:00.000 | 265.7 | 267.2 | 268.1 | 273.2 | 272.4 | 266.9 | 270.4 | 281.1 | 281.3 | 281.1 | 280.5 | 279.3 | 273.9333 | 281.3 | 265.7 | 264.2 | 275.6 | 270.3 | 260.4 | 258.9 | 280.8 | 280.9 | 281.3 | 280.5 | 280.4 | 281 | 280.8 | 274.5917 | 281.3 | 258.9 | 281.3 | 280.8 | 280.4 | 277.5 | 276.1 | 269.7 | 273.9 | 273.2 | 277.8 | 280.6 | 280.8 | 253.9 | 275.5 | 281.3 | 253.9
2026-05-13 | 12:00:00.000 | 263 | 265 | 266 | 271.8 | 271.3 | 265.7 | 269.9 | 281.1 | 281.3 | 281.4 | 280.9 | 281 | 273.2 | 281.4 | 263 | 263.6 | 275.4 | 270.1 | 260.4 | 259 | 281 | 280.7 | 271.6 | 270.9 | 281 | 281.3 | 281.2 | 273.0167 | 281.3 | 259 | 281.3 | 281.4 | 281.3 | 279.5 | 272.8 | 270.6 | 279.2 | 276.8 | 279.8 | 281.6 | 281.2 | 250.7 | 276.35 | 281.6 | 250.7
2026-05-13 | 12:15:00.000 | 270.6 | 272.6 | 272.3 | 271.7 | 273.6 | 272.6 | 264 | 281.1 | 274.1 | 281.3 | 276.7 | 281.9 | 274.375 | 281.9 | 264 | 253.8 | 263.2 | 259.6 | 245.7 | 241.5 | 276.9 | 272.6 | 278.4 | 273.5 | 269.6 | 268.4 | 272.8 | 264.6667 | 278.4 | 241.5 | 272.8 | 280.7 | 267.6 | 281.7 | 269 | 276.9 | 270.4 | 277.5 | 269.9 | 281.8 | 278.7 | 260.5 | 273.9583 | 281.8 | 260.5
2026-05-13 | 12:30:00.000 | 207.2 | 205.9 | 209 | 201.7 | 206.3 | 197.6 | 204.2 | 218 | 217.3 | 216.7 | 218.4 | 202.2 | 208.7083 | 218.4 | 197.6 | 197.9 | 203.9 | 192.4 | 199.2 | 199.8 | 210.1 | 204.2 | 218.1 | 203.5 | 208.4 | 207.4 | 207.5 | 204.3667 | 218.1 | 192.4 | 216.9 | 200.8 | 189.8 | 209.8 | 209.9 | 212.6 | 201 | 202.6 | 204.8 | 212 | 211.9 | 184.7 | 204.7333 | 216.9 | 184.7
2026-05-13 | 12:45:00.000 | 204.6 | 211.7 | 214.2 | 225.4 | 223.2 | 223.7 | 224.7 | 227.1 | 224.9 | 216.4 | 225.5 | 224.2 | 220.4667 | 227.1 | 204.6 | 218.8 | 222.2 | 215.3 | 216.7 | 215.8 | 213 | 204.9 | 213.9 | 209.9 | 206.8 | 220.2 | 220.3 | 214.8167 | 222.2 | 204.9 | 221.6 | 223.1 | 214.2 | 216 | 212 | 189.6 | 220 | 219.8 | 220.9 | 227.7 | 223.4 | 199.5 | 215.65 | 227.7 | 189.6
2026-05-13 | 13:00:00.000 | 170.3 | 193.3 | 186.4 | 186 | 184.2 | 182 | 179.7 | 217 | 198.7 | 199.7 | 200.6 | 203.9 | 191.8167 | 217 | 170.3 | 166.1 | 176.6 | 188.2 | 172.8 | 178.6 | 192.2 | 192 | 206.3 | 197 | 189.8 | 201.2 | 210.1 | 189.2417 | 210.1 | 166.1 | 197.2 | 206.4 | 200 | 205.8 | 203.8 | 192.3 | 198.7 | 198.4 | 198.8 | 204.3 | 203.1 | 189.6 | 199.8667 | 206.4 | 189.6
2026-05-13 | 13:15:00.000 | 163.5 | 185.3 | 176.1 | 190.6 | 185.8 | 174.3 | 184.1 | 202.2 | 206.3 | 194.9 | 202.6 | 194.4 | 188.3417 | 206.3 | 163.5 | 181.2 | 186.1 | 178 | 175.9 | 168.5 | 185.7 | 187.5 | 195 | 193.9 | 184.7 | 185.4 | 193.6 | 184.625 | 195 | 168.5 | 213.3 | 212.2 | 219.9 | 217.6 | 219.3 | 216.8 | 212.1 | 200.5 | 205.5 | 208.6 | 202.7 | 206.2 | 211.225 | 219.9 | 200.5
2026-05-13 | 13:30:00.000 | 186.9 | 195.5 | 211.1 | 206.5 | 202.6 | 199 | 217 | 217.3 | 228.2 | 221.6 | 222.9 | 223.6 | 211.0167 | 228.2 | 186.9 | 215.4 | 220.3 | 227.5 | 213.1 | 222.7 | 208.3 | 214.2 | 211.1 | 216.9 | 206.2 | 223.5 | 225.7 | 217.075 | 227.5 | 206.2 | 199.1 | 190.1 | 184.3 | 186 | 183.2 | 170.6 | 181.7 | 188.8 | 181 | 204.8 | 191.4 | 171.8 | 186.0667 | 204.8 | 170.6
2026-05-13 | 13:45:00.000 | 172.5 | 181.1 | 188.1 | 180.4 | 178.5 | 163.8 | 177 | 204.7 | 203.6 | 189.6 | 188.6 | 188.7 | 184.7167 | 204.7 | 163.8 | 172.7 | 174.2 | 179.5 | 162.5 | 164.5 | 191.2 | 185.9 | 174.5 | 171.6 | 164.1 | 180.3 | 186.5 | 175.625 | 191.2 | 162.5 | 203.3 | 198.3 | 226.3 | 226.2 | 235.5 | 233.7 | 223.4 | 225.5 | 196.4 | 226.1 | 215.1 | 234.8 | 220.3833 | 235.5 | 196.4
2026-05-13 | 14:00:00.000 | 251.8 | 251.3 | 234.3 | 241.8 | 244.4 | 252.2 | 233 | 254.3 | 244.6 | 251.2 | 253.4 | 244.6 | 246.4083 | 254.3 | 233 | 230.9 | 232.7 | 232.7 | 225.9 | 224.1 | 233.3 | 238.6 | 241.6 | 244.9 | 230.7 | 228.9 | 231.7 | 233 | 244.9 | 224.1 | 244.7 | 235.3 | 242.5 | 256.8 | 252.9 | 253.5 | 239.2 | 242.6 | 240.7 | 247.3 | 244.9 | 241.1 | 245.125 | 256.8 | 235.3
2026-05-13 | 14:15:00.000 | 254.7 | 262.1 | 257.3 | 248.7 | 256.9 | 257.8 | 267.5 | 270.1 | 260.9 | 265.3 | 265.9 | 269.4 | 261.3833 | 270.1 | 248.7 | 268.7 | 263.3 | 246.6 | 254.1 | 261.4 | 261.4 | 252.5 | 262.3 | 260.1 | 253.8 | 269.4 | 259.5 | 259.425 | 269.4 | 246.6 | 254.7 | 242.1 | 231.7 | 234.9 | 230.6 | 224.5 | 223.3 | 241.6 | 241.9 | 246.4 | 252.9 | 243.9 | 239.0417 | 254.7 | 223.3
2026-05-13 | 14:30:00.000 | 208.8 | 216.3 | 216.7 | 242.6 | 235.7 | 234.3 | 254.8 | 240.3 | 247.7 | 227.7 | 250 | 237.1 | 234.3333 | 254.8 | 208.8 | 233.8 | 249.7 | 258.8 | 255.7 | 254.2 | 236.1 | 245.5 | 239.9 | 249.6 | 253.5 | 255.9 | 259.5 | 249.35 | 259.5 | 233.8 | 233.2 | 225.8 | 222.7 | 227.3 | 216.4 | 207 | 190.5 | 201.8 | 221.3 | 230.9 | 214.4 | 185.3 | 214.7167 | 233.2 | 185.3
2026-05-13 | 14:45:00.000 | 234.2 | 242.4 | 248.6 | 242.4 | 237.8 | 227.8 | 220.9 | 244.6 | 250.7 | 245.8 | 246.3 | 238.5 | 240 | 250.7 | 220.9 | 221.7 | 228.5 | 227.9 | 214.7 | 210.9 | 226.4 | 252.3 | 236.2 | 244.8 | 232.6 | 239.2 | 249.2 | 232.0333 | 252.3 | 210.9 | 252.5 | 233.5 | 242 | 236.5 | 244.7 | 235.2 | 245.4 | 245.2 | 245.3 | 234.7 | 260.1 | 243.8 | 243.2417 | 260.1 | 233.5
2026-05-13 | 15:00:00.000 | 243.9 | 241.1 | 246.4 | 242.6 | 250.2 | 250 | 245.3 | 256.4 | 259 | 257 | 258.1 | 264.7 | 251.225 | 264.7 | 241.1 | 244 | 252.4 | 251.8 | 239.7 | 238.9 | 262.9 | 257.5 | 259 | 250.2 | 252.1 | 264.1 | 263.2 | 252.9833 | 264.1 | 238.9 | 253.6 | 244 | 250.8 | 225.8 | 249.1 | 239.8 | 247 | 238.6 | 235.5 | 241 | 254.3 | 224.1 | 241.9667 | 254.3 | 224.1
2026-05-13 | 15:15:00.000 | 229.2 | 241 | 241.6 | 250.1 | 242.7 | 238.1 | 249.2 | 247.6 | 256.7 | 252.3 | 259 | 251.4 | 246.575 | 259 | 229.2 | 247.4 | 258.2 | 233.9 | 243.2 | 231.6 | 251.9 | 258.2 | 251.6 | 249.3 | 238.5 | 260.1 | 260.9 | 248.7333 | 260.9 | 231.6 | 254.3 | 251.6 | 243.2 | 253.4 | 239.8 | 242.3 | 244.2 | 249.6 | 236.5 | 246.4 | 257.3 | 232 | 245.8833 | 257.3 | 232
2026-05-13 | 15:30:00.000 | 256 | 258.4 | 259.1 | 264.2 | 264.4 | 259.5 | 262.8 | 281.6 | 281.9 | 271.5 | 281.4 | 281.3 | 268.5083 | 281.9 | 256 | 258.5 | 260.3 | 262.4 | 252.5 | 251.5 | 280.4 | 274.4 | 280.6 | 267.3 | 267.5 | 281.7 | 271 | 267.3417 | 281.7 | 251.5 | 281 | 281.8 | 274.8 | 281.4 | 281.2 | 273.4 | 268.2 | 265.7 | 251.7 | 277.6 | 279.4 | 249.9 | 272.175 | 281.8 | 249.9
2026-05-13 | 15:45:00.000 | 242.7 | 256.5 | 257.6 | 261.9 | 260.9 | 257.6 | 261.1 | 281 | 281 | 281.4 | 280.6 | 269.7 | 266 | 281.4 | 242.7 | 256.2 | 267.3 | 259.9 | 250.8 | 249.5 | 279.7 | 264.4 | 280.7 | 260.5 | 272.7 | 281.1 | 279.1 | 266.825 | 281.1 | 249.5 | 277 | 281.2 | 277.3 | 281.5 | 281.6 | 272.1 | 278.5 | 268.2 | 273.4 | 280.7 | 280.6 | 239.9 | 274.3333 | 281.6 | 239.9
2026-05-13 | 16:00:00.000 | 255.4 | 258.5 | 259.4 | 263.9 | 264.3 | 258.3 | 260 | 281.2 | 281.2 | 281.2 | 281.3 | 281.8 | 268.875 | 281.8 | 255.4 | 249.3 | 266.2 | 260.9 | 247.5 | 250.1 | 280.3 | 275.4 | 281.3 | 261.9 | 281.3 | 271.4 | 281.7 | 267.275 | 281.7 | 247.5 | 281.2 | 281.1 | 278.9 | 281.3 | 281.8 | 274.3 | 277.3 | 270 | 265.6 | 281.2 | 281.7 | 250.4 | 275.4 | 281.8 | 250.4
2026-05-13 | 16:15:00.000 | 226.7 | 236.8 | 233.2 | 239.1 | 242.7 | 238 | 238.4 | 260.1 | 260.2 | 260.5 | 263.3 | 249.4 | 245.7 | 263.3 | 226.7 | 211.6 | 224.8 | 216.1 | 208.7 | 207.7 | 230.7 | 226.8 | 236.5 | 236.6 | 247.9 | 245.5 | 252.5 | 228.7833 | 252.5 | 207.7 | 276.3 | 275.3 | 280.3 | 281.2 | 271.6 | 275.1 | 279.2 | 270.7 | 276.7 | 281.4 | 276.2 | 251.1 | 274.5917 | 281.4 | 251.1
2026-05-13 | 16:30:00.000 | 182.9 | 186.5 | 178.4 | 187.5 | 191.6 | 182.3 | 185.2 | 220.1 | 228.3 | 213.7 | 216.8 | 216.7 | 199.1667 | 228.3 | 178.4 | 186.7 | 198.4 | 190.3 | 180.5 | 181.2 | 194.6 | 199.1 | 205.3 | 218.3 | 225.4 | 221.6 | 234.5 | 202.9917 | 234.5 | 180.5 | 273.2 | 264.3 | 272.3 | 274.4 | 274.1 | 244.4 | 264.7 | 262.8 | 273.5 | 280.5 | 270.9 | 246.5 | 266.8 | 280.5 | 244.4
2026-05-13 | 16:45:00.000 | 171.9 | 177.7 | 166.6 | 179.5 | 177.1 | 174.1 | 179.2 | 229.2 | 221.7 | 203.6 | 214 | 204.6 | 191.6 | 229.2 | 166.6 | 174.8 | 186.3 | 179.5 | 171.9 | 163.5 | 187.8 | 189.5 | 195.3 | 208.3 | 215.3 | 201.8 | 220.7 | 191.225 | 220.7 | 163.5 | 275.8 | 276.3 | 267.9 | 280.9 | 281.8 | 266.6 | 262.8 | 260.3 | 264.5 | 275.3 | 279.7 | 245.8 | 269.8083 | 281.8 | 245.8
2026-05-13 | 17:00:00.000 | 158.8 | 163.5 | 157.1 | 161 | 157.4 | 159.4 | 160.5 | 212.2 | 199 | 186.3 | 197.4 | 184.5 | 174.7583 | 212.2 | 157.1 | 155.9 | 166.5 | 159.7 | 153.9 | 152 | 169.3 | 175.3 | 174 | 191.4 | 194.7 | 189.8 | 204.3 | 173.9 | 204.3 | 152 | 280.1 | 265.4 | 262.6 | 271.2 | 266.9 | 257.6 | 262.6 | 253.4 | 260.2 | 272.6 | 270.6 | 235 | 263.1833 | 280.1 | 235
2026-05-13 | 17:15:00.000 | 149.9 | 150.1 | 147.5 | 152.4 | 152.8 | 147 | 152.8 | 194 | 187.5 | 170.1 | 181.8 | 179.6 | 163.7917 | 194 | 147 | 147.3 | 154.2 | 149.7 | 138.3 | 139.9 | 160.7 | 160.4 | 168.2 | 180.9 | 183 | 176.8 | 186.4 | 162.15 | 186.4 | 138.3 | 281.5 | 277.9 | 263.2 | 281.3 | 281.5 | 250.4 | 265.5 | 255.2 | 261 | 281.5 | 281.6 | 238.2 | 268.2333 | 281.6 | 238.2
2026-05-13 | 17:30:00.000 | 137.5 | 141.4 | 142.1 | 141.3 | 141.9 | 145.6 | 131.7 | 181.3 | 181.7 | 163.6 | 170.3 | 163 | 153.45 | 181.7 | 131.7 | 120.2 | 125 | 121.4 | 112.1 | 114.8 | 122.4 | 120.6 | 126.5 | 139.1 | 142.1 | 137 | 141.8 | 126.9167 | 142.1 | 112.1 | 213.2 | 224.8 | 197.1 | 215.3 | 218.7 | 192.1 | 192.4 | 190.4 | 188.9 | 222.2 | 211.7 | 183.1 | 204.1583 | 224.8 | 183.1
2026-05-13 | 17:45:00.000 | 179.5 | 170.3 | 175.2 | 168.6 | 172.2 | 176.6 | 178.2 | 239.2 | 221.2 | 210.9 | 217.5 | 202.1 | 192.625 | 239.2 | 168.6 | 116.4 | 125.8 | 117.7 | 113.8 | 115.5 | 122.4 | 122.3 | 130.3 | 137.7 | 139.7 | 138.8 | 145.9 | 127.1917 | 145.9 | 113.8 | 236.5 | 216.2 | 194.2 | 223.1 | 214.8 | 198.8 | 207.2 | 192.7 | 183.5 | 222.1 | 228.2 | 182.6 | 208.325 | 236.5 | 182.6
2026-05-13 | 18:00:00.000 | 152.7 | 155.7 | 147.3 | 155.1 | 148.7 | 144.8 | 151.3 | 202.6 | 199.5 | 181.5 | 189.2 | 176.6 | 167.0833 | 202.6 | 144.8 | 141.9 | 148.2 | 138.7 | 136.9 | 138.3 | 159.5 | 152.4 | 158.3 | 167.6 | 170.7 | 168.3 | 177.7 | 154.875 | 177.7 | 136.9 | 213.3 | 212.1 | 183.7 | 207.8 | 198.8 | 176.9 | 184.4 | 174.4 | 171.8 | 211.7 | 202.9 | 162.9 | 191.725 | 213.3 | 162.9
2026-05-13 | 18:15:00.000 | 114.9 | 119.8 | 116.7 | 119.7 | 117.8 | 117.4 | 119.9 | 163.6 | 156.7 | 143.4 | 152.4 | 138.4 | 131.725 | 163.6 | 114.9 | 119.3 | 121 | 121.8 | 106.5 | 113.8 | 127.5 | 114.6 | 127.7 | 137 | 137.1 | 130.3 | 138.9 | 124.625 | 138.9 | 106.5 | 163.1 | 156.9 | 137.1 | 147.2 | 134.1 | 121.3 | 123.7 | 128.6 | 139.2 | 168 | 157.9 | 121 | 141.5083 | 168 | 121
2026-05-13 | 18:30:00.000 | 90 | 94 | 96.5 | 95.8 | 98.3 | 88.4 | 86.5 | 117.4 | 119.7 | 119.7 | 121 | 112.2 | 103.2917 | 121 | 86.5 | 86.5 | 89.5 | 84.9 | 77 | 81.8 | 96.1 | 89 | 91.8 | 99.8 | 97.5 | 93.2 | 99.1 | 90.5167 | 99.8 | 77 | 128.2 | 126.7 | 105.1 | 116.8 | 113.2 | 101.5 | 108.9 | 97.2 | 109.3 | 134.2 | 122.8 | 97.1 | 113.4167 | 134.2 | 97.1
2026-05-13 | 18:45:00.000 | 65.8 | 62.9 | 62.6 | 56.4 | 61.3 | 60.6 | 55.6 | 85.2 | 77.4 | 78 | 80.4 | 72.1 | 68.1917 | 85.2 | 55.6 | 46.1 | 48.1 | 45.8 | 42.4 | 43.4 | 53 | 48.2 | 55.1 | 58 | 59.1 | 50.3 | 55.8 | 50.4417 | 59.1 | 42.4 | 97.2 | 83.6 | 79.3 | 87.8 | 86.2 | 76.4 | 86 | 82.8 | 81.5 | 95.6 | 89.3 | 69 | 84.5583 | 97.2 | 69
2026-05-13 | 19:00:00.000 | 42.2 | 42.9 | 41.9 | 44.8 | 45.3 | 42.4 | 41.8 | 60.1 | 59.1 | 53 | 57.1 | 52.9 | 48.625 | 60.1 | 41.8 | 40.4 | 43.5 | 41.4 | 37.3 | 38.4 | 43 | 42 | 44.7 | 47.4 | 49 | 48.3 | 51.6 | 43.9167 | 51.6 | 37.3 | 57.6 | 60 | 49.8 | 57.9 | 56 | 48.5 | 48.2 | 45.6 | 48.5 | 62.1 | 52.8 | 44 | 52.5833 | 62.1 | 44
2026-05-13 | 19:15:00.000 | 32.9 | 33.2 | 32.7 | 32.2 | 33.9 | 29.7 | 27.6 | 42.7 | 41.2 | 38.6 | 39.6 | 36.5 | 35.0667 | 42.7 | 27.6 | 28.8 | 29.5 | 27.4 | 25.2 | 25.9 | 31.3 | 31.6 | 33.3 | 36.2 | 37.4 | 36 | 39.8 | 31.8667 | 39.8 | 25.2 | 37.3 | 39.7 | 33.4 | 37.4 | 37.1 | 30.8 | 33.2 | 30.6 | 34 | 43 | 35.7 | 30.4 | 35.2167 | 43 | 30.4
2026-05-13 | 19:30:00.000 | 20.9 | 21.2 | 20.6 | 19.1 | 21.7 | 18.7 | 17.7 | 27.6 | 26.4 | 24.3 | 25.6 | 22.2 | 22.1667 | 27.6 | 17.7 | 18.9 | 18.6 | 18.4 | 17.8 | 18.9 | 20 | 22.3 | 23.7 | 26.3 | 27.3 | 26.5 | 28.7 | 22.2833 | 28.7 | 17.8 | 23.6 | 25.8 | 20.7 | 22.2 | 22.2 | 18.3 | 19.8 | 19.5 | 21 | 26.7 | 21.7 | 18.1 | 21.6333 | 26.7 | 18.1
2026-05-13 | 19:45:00.000 | 7.9 | 7.9 | 7.6 | 8 | 8 | 7.6 | 8.3 | 12.5 | 11.9 | 10.7 | 10.9 | 10.1 | 9.2833 | 12.5 | 7.6 | 9.1 | 9 | 8.9 | 8.7 | 9.6 | 10.7 | 11.4 | 11.9 | 14 | 14.5 | 13.7 | 14.8 | 11.3583 | 14.8 | 8.7 | 13.3 | 13.7 | 11.3 | 12.3 | 11.6 | 9.7 | 10.8 | 10.4 | 11.5 | 15 | 12.1 | 10.1 | 11.8167 | 15 | 9.7
2026-05-13 | 20:00:00.000 | 3.9 | 3.9 | 3.8 | 3.9 | 4 | 3.9 | 3.6 | 5 | 4.9 | 4.5 | 4.6 | 4.4 | 4.2 | 5 | 3.6 | 3.9 | 3.9 | 3.8 | 3.8 | 3.9 | 4.1 | 4.2 | 4.4 | 4.9 | 5 | 5 | 5 | 4.325 | 5 | 3.8 | 0.2 | 0.1 | 0.2 | 0.2 | 0.1 | 0.2 | 0.1 | 0.3 | 0.2 | 0.3 | 0.3 | 0.2 | 0.2 | 0.3 | 0.1
2026-05-13 | 20:15:00.000 | 1.1 | 0.9 | 1.2 | 1.2 | 1.2 | 1.3 | 1.2 | 1.5 | 1.5 | 1.4 | 1.5 | 1.4 | 1.2833 | 1.5 | 0.9 | 1.2 | 1.3 | 1 | 1.2 | 1 | 1.3 | 1.3 | 1.1 | 1.5 | 1.5 | 1.4 | 1.4 | 1.2667 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 20:30:00.000 | 0.1 | 0.1 | 0.2 | 0.1 | 0.4 | 0.2 | 0.2 | 0.3 | 0.3 | 0.2 | 0.1 | 0.5 | 0.225 | 0.5 | 0.1 | 0.2 | 0.3 | 0.1 | 0.2 | 0.8 | 0.2 | 0.3 | 0.9 | 0.4 | 0.3 | 0.1 | 0.7 | 0.375 | 0.9 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 20:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.125 | 0.3 | 0.1 | 0.1 | 0.1 | 0.7 | 0.1 | 0.4 | 0.1 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.5 | 0.23333 | 0.7 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.2 | 0 | 0 | 0 | 0.4 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-13 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320