## PR_Calc
PR CALCULATION
14 MAGGIO 2026 | [67 empty] | 14 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 51
RAW PR | [64 empty] | 0.76005 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 76.0054
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 75.9954
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 75.9971
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-14 | 00:00:00.000 | -1 | -0.00025 | -1.2 | -0.0003 | -0.000275 | 0 | -0.000275 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6556.5
2026-05-14 | 00:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 00:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 00:45:00.000 | -1 | -0.00025 | -1.5 | -0.000375 | -0.0003125 | 0 | -0.0003125 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 01:00:00.000 | -1 | -0.00025 | -1.3 | -0.000325 | -0.0002875 | 0 | -0.0002875 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 01:15:00.000 | -1 | -0.00025 | -1.1 | -0.000275 | -0.0002625 | 0 | -0.0002625 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 01:30:00.000 | -1 | -0.00025 | -1.1 | -0.000275 | -0.0002625 | 0 | -0.0002625 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 01:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 02:00:00.000 | -1 | -0.00025 | -1.2 | -0.0003 | -0.000275 | 0 | -0.000275 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 02:15:00.000 | -1 | -0.00025 | -1.3 | -0.000325 | -0.0002875 | 0 | -0.0002875 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 02:30:00.000 | -1 | -0.00025 | -1.4 | -0.00035 | -0.0003 | 0 | -0.0003 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 02:45:00.000 | -1.3 | -0.000325 | -2 | -0.0005 | -0.0004125 | 0 | -0.0004125 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 03:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 03:15:00.000 | -1.2 | -0.0003 | -1.5 | -0.000375 | -0.0003375 | 0 | -0.0003375 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 03:30:00.000 | -1.9 | -0.000475 | -2 | -0.0005 | -0.0004875 | 0 | -0.0004875 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 03:45:00.000 | -1.3 | -0.000325 | -1.8 | -0.00045 | -0.0003875 | 0 | -0.0003875 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 04:00:00.000 | -1.2 | -0.0003 | -1.2 | -0.0003 | -0.0003 | 0 | -0.0003 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 04:15:00.000 | -1.8 | -0.00045 | -2 | -0.0005 | -0.000475 | 0 | -0.000475 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 04:30:00.000 | -1 | -0.00025 | -1.1 | -0.000275 | -0.0002625 | 0 | -0.0002625 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 04:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 05:00:00.000 | -1.6 | -0.0004 | -1.4 | -0.00035 | -0.000375 | 0 | -0.000375 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 05:15:00.000 | -1.4 | -0.00035 | -1.3 | -0.000325 | -0.0003375 | 0 | -0.0003375 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 05:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 05:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 06:00:00.000 | 0.4 | 0.0001 | 0.1 | 2.5e-05 | 6.25e-05 | 0 | 6.25e-05 | 1.2 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 06:15:00.000 | 5.8 | 0.00145 | 5.4 | 0.00135 | 0.0014 | 0 | 0.0014 | 0.071429 | 31068.7 | 31068.7 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 06:30:00.000 | 14.3 | 0.003575 | 14.4 | 0.0036 | 0.0035875 | 0 | 0.0035875 | 0.0069686 | 31068.7 | 31068.8 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 06:45:00.000 | 33 | 0.00825 | 33.3 | 0.008325 | 0.0082875 | 0 | 0.0082875 | 0.0090498 | 31068.8 | 31068.8 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 07:00:00.000 | 80.9 | 0.020225 | 84.2 | 0.02105 | 0.020637 | 82.55 | 0.02105 | 0.039976 | 31068.8 | 31068.9 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 07:15:00.000 | 111.8 | 0.02795 | 112.2 | 0.02805 | 0.028 | 112 | 0.02805 | 0.0035714 | 31068.9 | 31069.1 | 200 | 0.876 | 6.8614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57178 | 6.8614 | 0 | 6.8614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 07:30:00.000 | 300.8 | 0.0752 | 324.3 | 0.081075 | 0.078137 | 312.55 | 0.081075 | 0.075188 | 31069.1 | 31069.6 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 07:45:00.000 | 427.3 | 0.10683 | 444.2 | 0.11105 | 0.10894 | 435.75 | 0.11105 | 0.038784 | 31069.6 | 31070.4 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 08:00:00.000 | 204 | 0.051 | 218.5 | 0.054625 | 0.052812 | 211.25 | 0.054625 | 0.068639 | 31070.4 | 31071.2 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 08:15:00.000 | 133 | 0.03325 | 135 | 0.03375 | 0.0335 | 134 | 0.03375 | 0.014925 | 31071.2 | 31071.6 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 08:30:00.000 | 251.1 | 0.062775 | 251.3 | 0.062825 | 0.0628 | 251.2 | 0.062825 | 0.00079618 | 31071.6 | 31072.1 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 08:45:00.000 | 551.1 | 0.13778 | 533.1 | 0.13328 | 0.13553 | 542.1 | 0.13778 | 0.033204 | 31072.1 | 31073 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 09:00:00.000 | 579.6 | 0.1449 | 552.1 | 0.13803 | 0.14146 | 565.85 | 0.1449 | 0.048599 | 31073 | 31074.5 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 09:15:00.000 | 586.9 | 0.14672 | 541.4 | 0.13535 | 0.14104 | 564.15 | 0.14672 | 0.080652 | 31074.5 | 31075.9 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 09:30:00.000 | 716.7 | 0.17918 | 635.3 | 0.15882 | 0.169 | 676 | 0.17918 | 0.12041 | 31075.9 | 31077.6 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 09:45:00.000 | 536.4 | 0.1341 | 588.7 | 0.14718 | 0.14064 | 562.55 | 0.14718 | 0.09297 | 31077.6 | 31079.2 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 10:00:00.000 | 830.3 | 0.20757 | 835.1 | 0.20878 | 0.20817 | 832.7 | 0.20878 | 0.0057644 | 31079.2 | 31080.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 10:15:00.000 | 620.5 | 0.15513 | 598.5 | 0.14963 | 0.15238 | 609.5 | 0.15513 | 0.036095 | 31080.7 | 31082.5 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 10:30:00.000 | 754.1 | 0.18852 | 681.3 | 0.17032 | 0.17943 | 717.7 | 0.18852 | 0.10144 | 31082.5 | 31084.2 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 10:45:00.000 | 761.2 | 0.1903 | 781.9 | 0.19547 | 0.19289 | 771.55 | 0.19547 | 0.026829 | 31084.2 | 31085.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 11:00:00.000 | 843.2 | 0.2108 | 829.6 | 0.2074 | 0.2091 | 836.4 | 0.2108 | 0.01626 | 31085.7 | 31087.5 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 11:15:00.000 | 950.8 | 0.2377 | 912.9 | 0.22822 | 0.23296 | 931.85 | 0.2377 | 0.040672 | 31087.5 | 31089.5 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 11:30:00.000 | 860.1 | 0.21502 | 850.4 | 0.2126 | 0.21381 | 855.25 | 0.21502 | 0.011342 | 31089.5 | 31091.7 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 11:45:00.000 | 640.5 | 0.16012 | 607.9 | 0.15197 | 0.15605 | 624.2 | 0.16012 | 0.052227 | 31091.7 | 31093.6 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 12:00:00.000 | 754.2 | 0.18855 | 724.3 | 0.18107 | 0.18481 | 739.25 | 0.18855 | 0.040446 | 31093.6 | 31095 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 12:15:00.000 | 996.5 | 0.24913 | 960.6 | 0.24015 | 0.24464 | 978.55 | 0.24913 | 0.036687 | 31095 | 31097.1 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 12:30:00.000 | 578.4 | 0.1446 | 550.4 | 0.1376 | 0.1411 | 564.4 | 0.1446 | 0.04961 | 31097.1 | 31098.9 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 12:45:00.000 | 574.6 | 0.14365 | 539 | 0.13475 | 0.1392 | 556.8 | 0.14365 | 0.063937 | 31098.9 | 31100.4 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 13:00:00.000 | 737.8 | 0.18445 | 559.2 | 0.1398 | 0.16212 | 648.5 | 0.18445 | 0.2754 | 31100.4 | 31102 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 13:15:00.000 | 565.7 | 0.14143 | 534.2 | 0.13355 | 0.13749 | 549.95 | 0.14143 | 0.057278 | 31102 | 31103.5 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 13:30:00.000 | 380.2 | 0.09505 | 378.3 | 0.094575 | 0.094812 | 379.25 | 0.09505 | 0.0050099 | 31103.5 | 31104.6 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 13:45:00.000 | 369.8 | 0.09245 | 389.3 | 0.097325 | 0.094888 | 379.55 | 0.097325 | 0.051377 | 31104.6 | 31105.6 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 14:00:00.000 | 535.4 | 0.13385 | 524.5 | 0.13112 | 0.13249 | 529.95 | 0.13385 | 0.020568 | 31105.6 | 31106.8 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 14:15:00.000 | 736.8 | 0.1842 | 674.8 | 0.1687 | 0.17645 | 705.8 | 0.1842 | 0.087844 | 31106.8 | 31108.1 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 14:30:00.000 | 734.2 | 0.18355 | 635.8 | 0.15895 | 0.17125 | 685 | 0.18355 | 0.14365 | 31108.1 | 31109.8 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 14:45:00.000 | 610.1 | 0.15252 | 508.7 | 0.12718 | 0.13985 | 559.4 | 0.15252 | 0.18127 | 31109.8 | 31111.2 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 15:00:00.000 | 379.1 | 0.094775 | 387.6 | 0.0969 | 0.095838 | 383.35 | 0.0969 | 0.022173 | 31111.2 | 31112.3 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 15:15:00.000 | 594.5 | 0.14863 | 526.4 | 0.1316 | 0.14011 | 560.45 | 0.14863 | 0.12151 | 31112.3 | 31113.4 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 15:30:00.000 | 758.1 | 0.18952 | 639 | 0.15975 | 0.17464 | 698.55 | 0.18952 | 0.1705 | 31113.4 | 31114.9 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 15:45:00.000 | 586.9 | 0.14672 | 658.3 | 0.16457 | 0.15565 | 622.6 | 0.16457 | 0.11468 | 31114.9 | 31116.2 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 16:00:00.000 | 690.4 | 0.1726 | 651.8 | 0.16295 | 0.16778 | 671.1 | 0.1726 | 0.057518 | 31116.2 | 31117.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 16:15:00.000 | 688.9 | 0.17222 | 718.7 | 0.17968 | 0.17595 | 703.8 | 0.17968 | 0.042342 | 31117.7 | 31119.2 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 16:30:00.000 | 343 | 0.08575 | 386.6 | 0.09665 | 0.0912 | 364.8 | 0.09665 | 0.11952 | 31119.2 | 31120.4 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 16:45:00.000 | 362.7 | 0.090675 | 382.3 | 0.095575 | 0.093125 | 372.5 | 0.095575 | 0.052617 | 31120.4 | 31121.3 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 17:00:00.000 | 696.7 | 0.17418 | 701.7 | 0.17542 | 0.1748 | 699.2 | 0.17542 | 0.007151 | 31121.3 | 31122.4 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 17:15:00.000 | 736.2 | 0.18405 | 667.7 | 0.16693 | 0.17549 | 701.95 | 0.18405 | 0.097585 | 31122.4 | 31124.2 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 17:30:00.000 | 587.7 | 0.14693 | 587.9 | 0.14697 | 0.14695 | 587.8 | 0.14697 | 0.00034025 | 31124.2 | 31125.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 17:45:00.000 | 340 | 0.085 | 341.3 | 0.085325 | 0.085163 | 340.65 | 0.085325 | 0.0038162 | 31125.7 | 31126.9 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 18:00:00.000 | 345.3 | 0.086325 | 362.6 | 0.09065 | 0.088487 | 353.95 | 0.09065 | 0.048877 | 31126.9 | 31127.7 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 18:15:00.000 | 308.6 | 0.07715 | 321.8 | 0.08045 | 0.0788 | 315.2 | 0.08045 | 0.041878 | 31127.7 | 31128.6 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 18:30:00.000 | 351.3 | 0.087825 | 387.5 | 0.096875 | 0.09235 | 369.4 | 0.096875 | 0.097997 | 31128.6 | 31129.4 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 18:45:00.000 | 172.9 | 0.043225 | 194.5 | 0.048625 | 0.045925 | 183.7 | 0.048625 | 0.11758 | 31129.4 | 31130.1 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 19:00:00.000 | 151.6 | 0.0379 | 173.3 | 0.043325 | 0.040612 | 162.45 | 0.043325 | 0.13358 | 31130.1 | 31130.5 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 19:15:00.000 | 100.5 | 0.025125 | 114.9 | 0.028725 | 0.026925 | 107.7 | 0.028725 | 0.1337 | 31130.5 | 31130.8 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 19:30:00.000 | 64.1 | 0.016025 | 73 | 0.01825 | 0.017137 | 68.55 | 0.01825 | 0.12983 | 31130.8 | 31131.1 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 19:45:00.000 | 37.9 | 0.009475 | 40.7 | 0.010175 | 0.009825 | 0 | 0.009825 | 0.071247 | 31131.1 | 31131.2 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 20:00:00.000 | 8.4 | 0.0021 | 8.4 | 0.0021 | 0.0021 | 0 | 0.0021 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 20:15:00.000 | 0.7 | 0.000175 | 0.3 | 7.5e-05 | 0.000125 | 0 | 0.000125 | 0.8 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 20:30:00.000 | -0.9 | -0.000225 | -0.9 | -0.000225 | -0.000225 | 0 | -0.000225 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 20:45:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 21:00:00.000 | -1.8 | -0.00045 | -1.8 | -0.00045 | -0.00045 | 0 | -0.00045 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 21:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 21:30:00.000 | -1.5 | -0.000375 | -1 | -0.00025 | -0.0003125 | 0 | -0.0003125 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 21:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 22:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 22:15:00.000 | -0.9 | -0.000225 | -0.6 | -0.00015 | -0.0001875 | 0 | -0.0001875 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 22:30:00.000 | -0.7 | -0.000175 | -0.4 | -0.0001 | -0.0001375 | 0 | -0.0001375 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 22:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 23:00:00.000 | -1 | -0.00025 | -0.9 | -0.000225 | -0.0002375 | 0 | -0.0002375 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
2026-05-14 | 23:45:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8864
PR for each inverter |  |  | 6.658 |  | 6.4584 | 6.5582 |  | 6.7757 |  |  |  | 62500 |  | 0.73179 | 0.73109 | 0.74034 | 0.74645 | 0.73881 | 0.7335 | 0.74677 | 0.80441 | 0.79405 | 0.76961 | 0.79007 | 0.81027 | #DIV/0! | #DIV/0! | #DIV/0! | 6.8614 | 0.75951 | 0.74577 | 0.74324 | 0.7502 | 0.7635 | 0.75892 | 0.78442 | 0.78044 | 0.79605 | 0.81579 | 0.77538 | 0.79687 |  |  |  | 0 | 0.79299 | 0.73397 | 0.71729 | 0.76718 | 0.75179 | 0.71192 | 0.73242 | 0.7148 | 0.71932 | 0.77865 | 0.77896 | 0.75182 | #DIV/0! | #DIV/0! | #DIV/0! | 0 |  | 0.75995 |  | #DIV/0! | #DIV/0! | 9.0605e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-14 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1.4 | 1.3 | 1.2 | 1.4 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.3 | 1.4 | 0.9 | 1.2167 | 1.4 | 0.9
2026-05-14 | 06:30:00.000 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 2 | 0 | 0.1 | 0 | 0 | 3.6 | 0 | 0 | 0 | 3.2 | 2.225 | 3.6 | 0 | 4.3 | 4.1 | 3.6 | 4.1 | 3.9 | 3.4 | 3.4 | 3.4 | 3.4 | 4.2 | 4.1 | 3 | 3.7417 | 4.3 | 3
2026-05-14 | 06:45:00.000 | 3.5 | 3.3 | 3.8 | 4.1 | 7 | 3.8 | 4 | 6.9 | 7.2 | 7.1 | 6.9 | 6 | 5.3 | 7.2 | 3.3 | 4.4 | 4 | 6.7 | 4.4 | 6.7 | 4.2 | 5.6 | 7.5 | 6.8 | 6.9 | 7.1 | 8.9 | 6.1 | 8.9 | 4 | 8.9 | 8.1 | 7.5 | 8.7 | 8.1 | 7.3 | 7.1 | 7.2 | 7.3 | 8.6 | 8.6 | 6.3 | 7.8083 | 8.9 | 6.3
2026-05-14 | 07:00:00.000 | 5.2 | 14.3 | 5.2 | 15.1 | 15.5 | 14.1 | 13.6 | 19.7 | 19.1 | 17.4 | 17.8 | 19.4 | 14.7 | 19.7 | 5.2 | 14.5 | 14.4 | 15 | 14.7 | 14.3 | 14.8 | 16.2 | 18 | 19.8 | 19.8 | 18.1 | 20.3 | 16.6583 | 20.3 | 14.3 | 20.8 | 18.7 | 17.8 | 20.9 | 19.5 | 17.8 | 18.7 | 18 | 17.5 | 19.7 | 20.6 | 16.3 | 18.8583 | 20.9 | 16.3
2026-05-14 | 07:15:00.000 | 0 | 23.7 | 21.8 | 25.8 | 27.5 | 25.7 | 27.6 | 28 | 30.6 | 29.2 | 30.9 | 31.1 | 27.4455 | 31.1 | 0 | 28.4 | 28.7 | 28.3 | 29.6 | 29.7 | 26 | 27.9 | 28.6 | 32.6 | 33.8 | 33.8 | 34.5 | 30.1583 | 34.5 | 26 | 31.2 | 28 | 25.6 | 28.6 | 26.7 | 23.8 | 25.6 | 25 | 25.2 | 28.8 | 29.8 | 22.5 | 26.7333 | 31.2 | 22.5
2026-05-14 | 07:30:00.000 | 58.8 | 67.1 | 70.3 | 68 | 70.3 | 67.4 | 66.1 | 86.2 | 84.9 | 81.7 | 86.7 | 83.4 | 74.2417 | 86.7 | 58.8 | 65.3 | 64.7 | 66.3 | 65.8 | 64.6 | 71.9 | 73.8 | 77.2 | 84.2 | 85.3 | 83.5 | 87.9 | 74.2083 | 87.9 | 64.6 | 91.9 | 85.6 | 78.1 | 93.8 | 89.9 | 82 | 80.5 | 77.7 | 76.8 | 88.4 | 89.2 | 72.2 | 83.8417 | 93.8 | 72.2
2026-05-14 | 07:45:00.000 | 100.6 | 101.9 | 98.3 | 102.3 | 96.1 | 89.9 | 93 | 134.3 | 126 | 119.5 | 129.2 | 117.8 | 109.075 | 134.3 | 89.9 | 91.8 | 89.7 | 90.7 | 86.4 | 86.7 | 107.7 | 111.6 | 113.2 | 125.5 | 125.4 | 120.4 | 127 | 106.3417 | 127 | 86.4 | 134.1 | 124.8 | 113 | 131.7 | 124.3 | 117.4 | 115.2 | 109.9 | 108.9 | 122.1 | 131.1 | 98.3 | 119.2333 | 134.1 | 98.3
2026-05-14 | 08:00:00.000 | 52.7 | 51.2 | 50.2 | 49.5 | 45.5 | 42.3 | 45.6 | 65.3 | 59.6 | 58.2 | 58.1 | 56.8 | 52.9167 | 65.3 | 42.3 | 43.5 | 43.2 | 41.9 | 40.4 | 41 | 51.7 | 49 | 51.5 | 53.8 | 53.1 | 52.1 | 52.9 | 47.8417 | 53.8 | 40.4 | 66.4 | 64.8 | 59.8 | 70.9 | 71.4 | 65.4 | 61.9 | 59.9 | 60.5 | 69.3 | 66.4 | 57.6 | 64.525 | 71.4 | 57.6
2026-05-14 | 08:15:00.000 | 34.9 | 35 | 35.6 | 36.8 | 36.9 | 36.5 | 37.4 | 45.9 | 44.8 | 42.6 | 45 | 43.8 | 39.6 | 45.9 | 34.9 | 37.1 | 39.1 | 38.5 | 37.3 | 36.9 | 40.3 | 40.3 | 42.1 | 45.4 | 45.8 | 45.1 | 48.2 | 41.3417 | 48.2 | 36.9 | 45.3 | 43.5 | 38.9 | 42.3 | 41.9 | 37 | 37.7 | 36.8 | 37.2 | 43.5 | 42.7 | 32.4 | 39.9333 | 45.3 | 32.4
2026-05-14 | 08:30:00.000 | 65.7 | 68.2 | 63.5 | 74.6 | 71.3 | 70.8 | 79.3 | 86.8 | 82.3 | 77.1 | 83.8 | 77 | 75.0333 | 86.8 | 63.5 | 72.5 | 79.9 | 78.1 | 77.3 | 71.7 | 77 | 72.7 | 77.8 | 81.1 | 82.3 | 86.9 | 89.9 | 78.9333 | 89.9 | 71.7 | 86.1 | 82.5 | 70.4 | 78.5 | 79.3 | 69.1 | 70.4 | 66.5 | 66.6 | 78.1 | 76 | 54.9 | 73.2 | 86.1 | 54.9
2026-05-14 | 08:45:00.000 | 138.1 | 138.6 | 139.5 | 146.9 | 143.2 | 141.1 | 146 | 167.7 | 167.5 | 158.9 | 164 | 163.1 | 151.2167 | 167.7 | 138.1 | 140.4 | 147.7 | 151.3 | 141.4 | 142.3 | 155.6 | 152.8 | 164 | 168.8 | 167 | 162.9 | 167.5 | 155.1417 | 168.8 | 140.4 | 157.7 | 159.2 | 143.9 | 149.8 | 147.7 | 136.4 | 131.2 | 128.4 | 140.5 | 157.5 | 154 | 117 | 143.6083 | 159.2 | 117
2026-05-14 | 09:00:00.000 | 155.2 | 152.6 | 163.9 | 154.5 | 157.8 | 149.2 | 156.6 | 168.6 | 170.7 | 169.9 | 163.2 | 163 | 160.4333 | 170.7 | 149.2 | 141.8 | 153.9 | 147.2 | 143.2 | 137.1 | 162.8 | 154 | 154.9 | 162.1 | 163 | 160.6 | 156.7 | 153.1083 | 163 | 137.1 | 170.6 | 152.7 | 153.5 | 164.3 | 160.5 | 142.6 | 160.2 | 152.7 | 145 | 155.2 | 171 | 149.7 | 156.5 | 171 | 142.6
2026-05-14 | 09:15:00.000 | 167.1 | 168.7 | 165.1 | 180.5 | 183 | 178.7 | 201.1 | 178.3 | 189.3 | 173.7 | 192.4 | 163.7 | 178.4667 | 201.1 | 163.7 | 183.8 | 192.1 | 189.9 | 189.4 | 185.9 | 184.7 | 166.3 | 187 | 190.6 | 181.3 | 194.8 | 195.5 | 186.775 | 195.5 | 166.3 | 144.1 | 160.4 | 167.4 | 152.5 | 152.7 | 143.6 | 159.5 | 148 | 155.5 | 160.3 | 154.7 | 139.7 | 153.2 | 167.4 | 139.7
2026-05-14 | 09:30:00.000 | 194.5 | 195.6 | 185.8 | 199.7 | 192.9 | 197.4 | 202.9 | 208.9 | 207.1 | 199.2 | 208.7 | 205.6 | 199.8583 | 208.9 | 185.8 | 197.4 | 190.5 | 199.9 | 189.5 | 186.8 | 197.2 | 201.5 | 198 | 205.7 | 206.6 | 209.1 | 207.9 | 199.175 | 209.1 | 186.8 | 187.1 | 186.6 | 155.6 | 184.4 | 181 | 191.3 | 176.7 | 171 | 173.7 | 180.5 | 180 | 154.7 | 176.8833 | 191.3 | 154.7
2026-05-14 | 09:45:00.000 | 145.1 | 143.7 | 140.7 | 148.2 | 127.9 | 137.6 | 154.9 | 154.7 | 149.7 | 148.7 | 143.9 | 151 | 145.5083 | 154.9 | 127.9 | 128.7 | 142.7 | 149.3 | 138.1 | 137.6 | 140.4 | 133.1 | 136.2 | 143.4 | 150.6 | 144.2 | 150 | 141.1917 | 150.6 | 128.7 | 160.7 | 145.8 | 150.9 | 165.1 | 164.7 | 163.2 | 168.2 | 164.2 | 164.2 | 167 | 154.6 | 152.8 | 160.1167 | 168.2 | 145.8
2026-05-14 | 10:00:00.000 | 205.5 | 203.2 | 196.4 | 199.6 | 204.8 | 196.1 | 206.6 | 211.9 | 213.7 | 206.7 | 210.7 | 197.7 | 204.4083 | 213.7 | 196.1 | 186.6 | 199.6 | 194.8 | 194.4 | 192.4 | 207.5 | 203.8 | 184.6 | 198.5 | 211.1 | 210.2 | 215.4 | 199.9083 | 215.4 | 184.6 | 213.7 | 221.1 | 209.8 | 211.2 | 203.3 | 203.7 | 197.5 | 206.7 | 215 | 222.4 | 224.1 | 211.6 | 211.675 | 224.1 | 197.5
2026-05-14 | 10:15:00.000 | 160.1 | 153.6 | 162.9 | 164.9 | 166.2 | 154.7 | 171 | 162.1 | 163.4 | 160.9 | 164.2 | 168 | 162.6667 | 171 | 153.6 | 163.3 | 164.2 | 172.4 | 158 | 167.7 | 152.3 | 146.6 | 156.5 | 160.1 | 154.7 | 155.5 | 156 | 158.9417 | 172.4 | 146.6 | 150.8 | 165.2 | 158.2 | 169.2 | 147.7 | 166.9 | 151 | 161 | 150.1 | 168.8 | 161.2 | 162.1 | 159.35 | 169.2 | 147.7
2026-05-14 | 10:30:00.000 | 204.3 | 192.1 | 190.3 | 206.3 | 187.2 | 198.3 | 207 | 207.2 | 205 | 199.1 | 209.9 | 200.1 | 200.5667 | 209.9 | 187.2 | 201.1 | 204.4 | 188.8 | 194.8 | 197.4 | 195.7 | 190 | 192.6 | 202.5 | 198.6 | 202.2 | 200.2 | 197.3583 | 204.4 | 188.8 | 173.8 | 184.5 | 179.7 | 179.2 | 179.4 | 173.1 | 181.6 | 185.6 | 183 | 193.7 | 184.4 | 191.5 | 182.4583 | 193.7 | 173.1
2026-05-14 | 10:45:00.000 | 185.9 | 185.2 | 188.9 | 189.9 | 172.8 | 174 | 164.8 | 194.4 | 199.4 | 194 | 200.4 | 195.8 | 187.125 | 200.4 | 164.8 | 167.6 | 171.6 | 163.5 | 158.4 | 151 | 198.1 | 194.4 | 179.6 | 195.6 | 199.5 | 192.7 | 201 | 181.0833 | 201 | 151 | 215 | 206.1 | 189 | 195.4 | 195.7 | 189.1 | 195.7 | 192.1 | 190.4 | 198.9 | 208 | 189.6 | 197.0833 | 215 | 189
2026-05-14 | 11:00:00.000 | 208.7 | 205.7 | 210.1 | 200 | 189.6 | 190.9 | 197.1 | 221 | 217.7 | 212.7 | 213 | 220.1 | 207.2167 | 221 | 189.6 | 188.6 | 195.8 | 191.5 | 192.7 | 184.6 | 214 | 211.4 | 208.7 | 217.8 | 211.7 | 204.2 | 203.4 | 202.0333 | 217.8 | 184.6 | 229.8 | 221 | 209.6 | 211.4 | 213.4 | 209.4 | 230.5 | 201.2 | 210.3 | 218.8 | 217.4 | 210.3 | 215.2583 | 230.5 | 201.2
2026-05-14 | 11:15:00.000 | 237.3 | 229.2 | 249.6 | 243.1 | 246.6 | 240 | 253 | 250.6 | 252.9 | 249.4 | 250.8 | 254.2 | 246.3917 | 254.2 | 229.2 | 235.1 | 244.7 | 246.9 | 236.4 | 238.9 | 248.8 | 245.9 | 244.4 | 254 | 252.8 | 251.1 | 251.6 | 245.8833 | 254 | 235.1 | 242.7 | 241.3 | 237.7 | 228.4 | 219.4 | 211 | 241.5 | 237.6 | 224.3 | 238.6 | 254.2 | 225.1 | 233.4833 | 254.2 | 211
2026-05-14 | 11:30:00.000 | 223.9 | 226.2 | 215.3 | 232.9 | 234.1 | 231.6 | 238.7 | 239.7 | 243 | 240.8 | 232 | 242.1 | 233.3583 | 243 | 215.3 | 230.3 | 241.5 | 238.9 | 234.6 | 231.2 | 239.6 | 227.3 | 242.5 | 244.4 | 242.6 | 246.2 | 247.3 | 238.8667 | 247.3 | 227.3 | 246 | 242.8 | 229.4 | 243.5 | 243.3 | 229.7 | 240.1 | 237.6 | 239.7 | 242.8 | 241.9 | 219.6 | 238.0333 | 246 | 219.6
2026-05-14 | 11:45:00.000 | 165.6 | 165.7 | 165.3 | 166.9 | 157.6 | 163.5 | 165.7 | 188.3 | 184.3 | 178.4 | 179.3 | 178.5 | 171.5917 | 188.3 | 157.6 | 161.6 | 165.3 | 163.8 | 158.5 | 157.7 | 167.7 | 163.8 | 179.6 | 181.4 | 176.4 | 175.2 | 179.5 | 169.2083 | 181.4 | 157.7 | 182 | 180.1 | 168.4 | 180.9 | 178.6 | 167.7 | 174.1 | 169.5 | 169 | 183.9 | 181 | 166.9 | 175.175 | 183.9 | 166.9
2026-05-14 | 12:00:00.000 | 174 | 172.1 | 181.7 | 181.9 | 186 | 184.6 | 182.5 | 202.4 | 201.9 | 196.5 | 200.1 | 199 | 188.5583 | 202.4 | 172.1 | 185.6 | 182.4 | 189.8 | 188.8 | 188.7 | 186 | 181.8 | 206.6 | 209.1 | 204.3 | 190.4 | 213 | 193.875 | 213 | 181.8 | 204.1 | 194 | 186.9 | 194.6 | 186.2 | 174.6 | 178.8 | 181.3 | 181.3 | 194.6 | 194.5 | 160.1 | 185.9167 | 204.1 | 160.1
2026-05-14 | 12:15:00.000 | 239.6 | 238.4 | 242.5 | 238.7 | 236.2 | 232.6 | 231.7 | 262.6 | 256.5 | 255.7 | 257.5 | 252.7 | 245.3917 | 262.6 | 231.7 | 230.3 | 234.5 | 233.3 | 224.6 | 217.4 | 247.1 | 233 | 256.7 | 256 | 250.7 | 247.8 | 255.9 | 240.6083 | 256.7 | 217.4 | 261.6 | 263.1 | 242.9 | 263.9 | 257.1 | 250.2 | 254.2 | 250 | 246 | 263.5 | 251.6 | 238.2 | 253.525 | 263.9 | 238.2
2026-05-14 | 12:30:00.000 | 157.2 | 158.6 | 155.4 | 159 | 155.5 | 156.8 | 157.3 | 184.1 | 184.2 | 173.5 | 181 | 174.5 | 166.425 | 184.2 | 155.4 | 151.2 | 156.2 | 152.3 | 149.1 | 144.6 | 161.4 | 158.9 | 181.7 | 181.8 | 174.2 | 173.2 | 180.4 | 163.75 | 181.8 | 144.6 | 181.9 | 175.3 | 158.2 | 174.7 | 175.4 | 160.3 | 166.7 | 160.1 | 161.2 | 183.4 | 177.5 | 150.5 | 168.7667 | 183.4 | 150.5
2026-05-14 | 12:45:00.000 | 155.5 | 155.4 | 154.9 | 155 | 147.9 | 154.8 | 159 | 190.7 | 184.5 | 173.4 | 181.1 | 165.3 | 164.7917 | 190.7 | 147.9 | 149.6 | 161.3 | 151.4 | 154.6 | 149.9 | 155.1 | 166 | 181 | 183.6 | 178.3 | 175.4 | 181.4 | 165.6333 | 183.6 | 149.6 | 181.3 | 175.4 | 157.6 | 164.5 | 161 | 141.8 | 160.6 | 154.3 | 156.4 | 177.8 | 175.4 | 144 | 162.5083 | 181.3 | 141.8
2026-05-14 | 13:00:00.000 | 182 | 186.8 | 194.1 | 192.9 | 202.7 | 196.6 | 201.1 | 205.1 | 197.8 | 185.6 | 205.7 | 207.4 | 196.4833 | 207.4 | 182 | 196 | 192.1 | 202.2 | 187.3 | 189.6 | 187.2 | 197.2 | 208.9 | 207.5 | 206.6 | 201.7 | 209.6 | 198.825 | 209.6 | 187.2 | 179.3 | 169 | 149.7 | 148.2 | 152.7 | 132.2 | 150.2 | 152.2 | 159.4 | 160.4 | 182 | 151.6 | 157.2417 | 182 | 132.2
2026-05-14 | 13:15:00.000 | 140.2 | 139.9 | 143.4 | 143.7 | 132.2 | 135.7 | 133.9 | 169.7 | 167 | 156.3 | 165.3 | 165.6 | 149.4083 | 169.7 | 132.2 | 138.2 | 140.9 | 139.4 | 133.8 | 136.6 | 154.1 | 161.1 | 175.7 | 174.5 | 165.9 | 167.3 | 176 | 155.2917 | 176 | 133.8 | 169.9 | 164.8 | 150.1 | 167.2 | 158.8 | 148.6 | 151.6 | 150.2 | 141.8 | 168.8 | 166.3 | 139.8 | 156.4917 | 169.9 | 139.8
2026-05-14 | 13:30:00.000 | 105.5 | 104.6 | 99.8 | 102.1 | 101.5 | 100.8 | 96.2 | 127.1 | 127.5 | 112.3 | 121.6 | 109.8 | 109.0667 | 127.5 | 96.2 | 98.9 | 102.6 | 98.3 | 99.3 | 96.7 | 109.4 | 114.1 | 127.3 | 130.4 | 117.6 | 108.5 | 124.5 | 110.6333 | 130.4 | 96.7 | 123.6 | 121.3 | 108.2 | 120 | 115.8 | 104.7 | 111.3 | 108.6 | 108.2 | 128 | 115.6 | 100.3 | 113.8 | 128 | 100.3
2026-05-14 | 13:45:00.000 | 96.6 | 97.1 | 100.2 | 100.1 | 100.8 | 98.4 | 98.2 | 119.2 | 119.8 | 116.6 | 117.8 | 116.6 | 106.7833 | 119.8 | 96.6 | 99.8 | 97 | 104.7 | 93.2 | 96.2 | 112 | 120 | 126 | 124 | 119.7 | 117.2 | 123.5 | 111.1083 | 126 | 93.2 | 128.9 | 123.9 | 111.9 | 127.7 | 118.9 | 109.4 | 107.8 | 107.1 | 108.7 | 122.6 | 120 | 94.5 | 115.1167 | 128.9 | 94.5
2026-05-14 | 14:00:00.000 | 126.6 | 128.1 | 138.2 | 131.6 | 136.8 | 138 | 134.6 | 154.3 | 144.8 | 148.8 | 147.9 | 155.5 | 140.4333 | 155.5 | 126.6 | 136.7 | 136.2 | 135.5 | 128.7 | 129.4 | 151.8 | 144.1 | 153 | 150.7 | 146.6 | 155.9 | 159.1 | 143.975 | 159.1 | 128.7 | 156.4 | 149.5 | 134.2 | 152.2 | 145 | 141.1 | 129.7 | 129.4 | 129.1 | 144.3 | 147.1 | 130.3 | 140.6917 | 156.4 | 129.1
2026-05-14 | 14:15:00.000 | 168.8 | 165.9 | 173.2 | 170.2 | 168.9 | 169.3 | 162.8 | 191.5 | 186.8 | 181.1 | 194.2 | 180 | 176.0583 | 194.2 | 162.8 | 160.4 | 172.8 | 164.3 | 157.6 | 154.6 | 177 | 185.6 | 190.9 | 199.5 | 189.9 | 188.8 | 182.7 | 177.0083 | 199.5 | 154.6 | 182.3 | 166.6 | 160.4 | 180.1 | 175.6 | 164.8 | 169.4 | 164.5 | 155.7 | 176.4 | 178 | 150.6 | 168.7 | 182.3 | 150.6
2026-05-14 | 14:30:00.000 | 169.2 | 170.4 | 172.1 | 170.2 | 173.5 | 172.3 | 162.4 | 188.4 | 181.6 | 192 | 189.2 | 185.9 | 177.2667 | 192 | 162.4 | 155.3 | 164.2 | 172.4 | 160.2 | 160.3 | 185.9 | 179.6 | 187.6 | 181.7 | 180.7 | 180.5 | 169.6 | 173.1667 | 187.6 | 155.3 | 174.1 | 146.9 | 154.4 | 157.3 | 165.8 | 160.4 | 171.1 | 169.1 | 169.7 | 170.9 | 168.8 | 170.4 | 164.9083 | 174.1 | 146.9
2026-05-14 | 14:45:00.000 | 142.3 | 142.6 | 154.9 | 140.9 | 154.5 | 146.8 | 139.7 | 158.3 | 149.5 | 158.3 | 148.5 | 158.7 | 149.5833 | 158.7 | 139.7 | 143.9 | 145.5 | 145.8 | 135.1 | 140.8 | 155.5 | 149.6 | 149.2 | 145.5 | 148.3 | 143.4 | 153.9 | 146.375 | 155.5 | 135.1 | 135.9 | 123.8 | 139.9 | 145.6 | 132.5 | 129.6 | 134.5 | 139.9 | 145.4 | 148.9 | 137.3 | 135.2 | 137.375 | 148.9 | 123.8
2026-05-14 | 15:00:00.000 | 92.5 | 93.9 | 91.5 | 98 | 93.7 | 94.6 | 97.3 | 116.4 | 114.5 | 109.3 | 109.8 | 109.6 | 101.7583 | 116.4 | 91.5 | 95.5 | 99.6 | 92.9 | 93.4 | 93.6 | 117.8 | 112.6 | 120.6 | 117.7 | 113.2 | 117.3 | 121.8 | 108 | 121.8 | 92.9 | 120.3 | 109.8 | 108.6 | 114.7 | 112 | 101.5 | 107.9 | 99.7 | 104.9 | 117.1 | 113.3 | 89.3 | 108.2583 | 120.3 | 89.3
2026-05-14 | 15:15:00.000 | 143.3 | 146.5 | 151.2 | 153.6 | 145.4 | 149.8 | 160.6 | 160.2 | 165.1 | 159.6 | 156.4 | 155.6 | 153.9417 | 165.1 | 143.3 | 162.1 | 161 | 159.3 | 154.6 | 157.2 | 158.8 | 149.6 | 161.2 | 160.9 | 155.3 | 164 | 163.1 | 158.925 | 164 | 149.6 | 158.7 | 129.2 | 131.7 | 151.6 | 146.1 | 134.6 | 146.8 | 129.1 | 139.6 | 148.7 | 149.5 | 135.1 | 141.725 | 158.7 | 129.1
2026-05-14 | 15:30:00.000 | 176.7 | 174.3 | 182.8 | 159.5 | 170.5 | 173.5 | 178.4 | 186.3 | 183.4 | 182.9 | 187.3 | 185.1 | 178.3917 | 187.3 | 159.5 | 174.6 | 175.5 | 173.8 | 164.2 | 171.7 | 179.1 | 185.3 | 186.1 | 186.5 | 186.5 | 183.9 | 184.3 | 179.2917 | 186.5 | 164.2 | 159.4 | 126.7 | 142.6 | 168.2 | 171.4 | 158.5 | 165.4 | 159.1 | 153.5 | 158.1 | 180.3 | 173.5 | 159.725 | 180.3 | 126.7
2026-05-14 | 15:45:00.000 | 129.2 | 134.1 | 135.7 | 143.5 | 135.6 | 136.4 | 147.1 | 156.8 | 148.2 | 152.9 | 158.2 | 150.5 | 144.0167 | 158.2 | 129.2 | 141.1 | 136 | 146.3 | 137.8 | 137 | 162.3 | 158.7 | 157.3 | 155.2 | 160.4 | 156.6 | 170.8 | 151.625 | 170.8 | 136 | 174.8 | 133.1 | 147.2 | 157.8 | 162.3 | 152.4 | 154.6 | 151 | 148.3 | 151.6 | 173.7 | 140.6 | 153.95 | 174.8 | 133.1
2026-05-14 | 16:00:00.000 | 161.1 | 162 | 166.2 | 160.9 | 154.6 | 163.7 | 161 | 177.3 | 167.8 | 171.1 | 175.8 | 165.7 | 165.6 | 177.3 | 154.6 | 161.2 | 168.3 | 160.7 | 155.2 | 149.7 | 171.6 | 165.8 | 173.6 | 172.2 | 157.1 | 166.3 | 171.5 | 164.4333 | 173.6 | 149.7 | 183.9 | 135.2 | 155.9 | 153.7 | 156.2 | 156.4 | 169.6 | 157.8 | 153.3 | 161 | 182.2 | 170.7 | 161.325 | 183.9 | 135.2
2026-05-14 | 16:15:00.000 | 156.4 | 156.3 | 150.1 | 159.2 | 154.5 | 168.4 | 156.9 | 178.8 | 179.8 | 179.9 | 182.3 | 189.5 | 167.675 | 189.5 | 150.1 | 158.7 | 165.1 | 163.9 | 152.8 | 149.7 | 200.6 | 193.3 | 197.7 | 194 | 189.9 | 190 | 189.4 | 178.7583 | 200.6 | 149.7 | 189.8 | 148 | 173.4 | 185.1 | 188.8 | 184.5 | 178.1 | 165.6 | 163.6 | 182.6 | 177.8 | 176.1 | 176.1167 | 189.8 | 148
2026-05-14 | 16:30:00.000 | 82.9 | 82 | 84.5 | 86.4 | 89.3 | 82.2 | 83.9 | 97.5 | 105.2 | 89.9 | 99.2 | 94.7 | 89.8083 | 105.2 | 82 | 86 | 88.8 | 88 | 84.4 | 93.5 | 91.8 | 103.4 | 99.9 | 104.5 | 104 | 97 | 104.9 | 95.5167 | 104.9 | 84.4 | 103.4 | 97.5 | 114.8 | 111.1 | 103.5 | 90.5 | 90.6 | 102.6 | 109.2 | 105.5 | 91.9 | 85.8 | 100.5333 | 114.8 | 85.8
2026-05-14 | 16:45:00.000 | 81.3 | 81.1 | 84.4 | 82 | 81 | 76 | 82.6 | 101 | 100.2 | 97.3 | 95.5 | 106.9 | 89.1083 | 106.9 | 76 | 82.3 | 83.7 | 85.5 | 80.9 | 96 | 105.7 | 94 | 106.7 | 105.6 | 100.6 | 106.8 | 112 | 96.65 | 112 | 80.9 | 114.9 | 105.1 | 96.8 | 124.7 | 114.5 | 117.5 | 109.8 | 106.2 | 104.4 | 116.2 | 106.1 | 84.8 | 108.4167 | 124.7 | 84.8
2026-05-14 | 17:00:00.000 | 168.3 | 170.2 | 163.9 | 163 | 162.4 | 160.4 | 161 | 198.1 | 203.9 | 179.2 | 193.5 | 182.5 | 175.5333 | 203.9 | 160.4 | 152.1 | 158.3 | 161 | 150.9 | 167.1 | 194.4 | 190.2 | 173.4 | 192.1 | 190 | 195.2 | 187.8 | 176.0417 | 195.2 | 150.9 | 202.5 | 139.5 | 185.6 | 188.7 | 187.7 | 180.5 | 179.7 | 176 | 186.6 | 200.3 | 204.4 | 177.1 | 184.05 | 204.4 | 139.5
2026-05-14 | 17:15:00.000 | 183.1 | 178.6 | 190.6 | 175.3 | 191.1 | 177.6 | 175.4 | 195.1 | 181.1 | 189.8 | 182.7 | 192.6 | 184.4167 | 195.1 | 175.3 | 159.5 | 175.1 | 167 | 165.2 | 180.7 | 181.7 | 182.6 | 192.2 | 193.8 | 183.4 | 176.2 | 175.3 | 177.725 | 193.8 | 159.5 | 188 | 136.7 | 180.2 | 192.2 | 191.4 | 184.6 | 184.3 | 182 | 189.1 | 195.2 | 197.7 | 187.1 | 184.0417 | 197.7 | 136.7
2026-05-14 | 17:30:00.000 | 132.1 | 129.6 | 147 | 147.4 | 143.1 | 148.2 | 142.4 | 182.3 | 179 | 166.7 | 178.4 | 167.9 | 155.3417 | 182.3 | 129.6 | 147.2 | 139.2 | 151.3 | 142 | 163.6 | 164.5 | 161.9 | 178.4 | 179.1 | 174 | 174 | 183.3 | 163.2083 | 183.3 | 139.2 | 182.4 | 142.6 | 153.2 | 166.5 | 170.3 | 152.7 | 152.9 | 146.8 | 152.4 | 167.8 | 174.7 | 134.7 | 158.0833 | 182.4 | 134.7
2026-05-14 | 17:45:00.000 | 86.6 | 87.7 | 88.2 | 89.1 | 89.3 | 87.4 | 89.4 | 114.2 | 111.3 | 102.9 | 108.2 | 103.9 | 96.5167 | 114.2 | 86.6 | 79.9 | 89.1 | 87.8 | 85.2 | 97 | 98.9 | 105.8 | 110.3 | 111.9 | 107.3 | 104.9 | 111.4 | 99.125 | 111.9 | 79.9 | 114.9 | 102.4 | 96 | 106.1 | 101.4 | 91.5 | 95 | 94.3 | 96.7 | 111.6 | 108.1 | 88.7 | 100.5583 | 114.9 | 88.7
2026-05-14 | 18:00:00.000 | 86.8 | 88 | 86.3 | 88.2 | 89.9 | 85.7 | 85.4 | 112.5 | 109.5 | 105.9 | 108.4 | 103.1 | 95.8083 | 112.5 | 85.4 | 87.4 | 88.6 | 87.7 | 83.6 | 92 | 99.5 | 104.2 | 110.4 | 110.3 | 103.6 | 102.5 | 107.3 | 98.0917 | 110.4 | 83.6 | 113 | 109.2 | 95 | 109.3 | 107.9 | 93.7 | 99.6 | 93.8 | 93.7 | 109.9 | 108.6 | 85.9 | 101.6333 | 113 | 85.9
2026-05-14 | 18:15:00.000 | 80.3 | 81 | 77.2 | 81.3 | 80 | 77 | 77.9 | 100.2 | 99 | 95.1 | 98.5 | 95.2 | 86.8917 | 100.2 | 77 | 80.2 | 81.8 | 76.8 | 75.7 | 88.5 | 96.2 | 91.5 | 99 | 97.9 | 91.1 | 88.2 | 95.9 | 88.5667 | 99 | 75.7 | 102.4 | 91.7 | 84.6 | 88.3 | 82.5 | 82.3 | 86.7 | 83.7 | 86.4 | 99.3 | 97.6 | 78.6 | 88.675 | 102.4 | 78.6
2026-05-14 | 18:30:00.000 | 88.4 | 89.4 | 90.2 | 90.6 | 92.7 | 89.9 | 87.2 | 120.6 | 116.5 | 109.5 | 116.7 | 106.6 | 99.8583 | 120.6 | 87.2 | 87.5 | 92 | 88.4 | 86.3 | 99 | 105.7 | 108.8 | 105.1 | 110.5 | 104.9 | 102.5 | 108.6 | 99.9417 | 110.5 | 86.3 | 122.6 | 115 | 101.1 | 110.4 | 106.9 | 96.2 | 99.3 | 97.1 | 101.3 | 121.1 | 114.6 | 90.9 | 106.375 | 122.6 | 90.9
2026-05-14 | 18:45:00.000 | 43.7 | 44.3 | 43.8 | 45.1 | 44.9 | 43.6 | 44.1 | 59.8 | 58.4 | 54.1 | 56.7 | 54.2 | 49.3917 | 59.8 | 43.6 | 43.6 | 45.3 | 44.4 | 42.1 | 48.4 | 53.9 | 54.1 | 54.5 | 56.2 | 53.3 | 51.4 | 54.9 | 50.175 | 56.2 | 42.1 | 60.7 | 59.7 | 51.3 | 57.7 | 56 | 49.3 | 49.7 | 49.8 | 50.7 | 60.8 | 58.3 | 45 | 54.0833 | 60.8 | 45
2026-05-14 | 19:00:00.000 | 38.9 | 39.3 | 39.3 | 40.1 | 40.3 | 39.1 | 39.4 | 53.5 | 51.9 | 48.5 | 51.2 | 48.2 | 44.1417 | 53.5 | 38.9 | 39.1 | 40.9 | 39.8 | 37.5 | 43.2 | 47.6 | 47.8 | 49.5 | 49.3 | 46.6 | 45 | 48.1 | 44.5333 | 49.5 | 37.5 | 53.6 | 52.3 | 45.5 | 50.7 | 48.8 | 43.3 | 45.1 | 43.9 | 45.3 | 54.4 | 51.1 | 40.2 | 47.85 | 54.4 | 40.2
2026-05-14 | 19:15:00.000 | 25.8 | 26 | 25.9 | 26.6 | 26.6 | 25.8 | 26.5 | 35.6 | 34.6 | 32.3 | 33.8 | 32.2 | 29.3083 | 35.6 | 25.8 | 25.7 | 27 | 26.2 | 24.8 | 28.5 | 31.5 | 31.9 | 33 | 32.9 | 31.1 | 30.1 | 32.2 | 29.575 | 33 | 24.8 | 35.5 | 34.7 | 30.3 | 34 | 32.9 | 28.7 | 29.8 | 28.9 | 29.8 | 35.9 | 33.6 | 26.4 | 31.7083 | 35.9 | 26.4
2026-05-14 | 19:30:00.000 | 16.3 | 16.3 | 16.3 | 16.8 | 16.8 | 16.4 | 17.1 | 22.7 | 22.1 | 20.6 | 21.6 | 20.6 | 18.6333 | 22.7 | 16.3 | 16.2 | 17.1 | 16.6 | 15.6 | 17.9 | 19.8 | 20.1 | 20.8 | 20.7 | 19.6 | 19.1 | 20.4 | 18.6583 | 20.8 | 15.6 | 22.4 | 22 | 19.3 | 21.6 | 21 | 18.1 | 18.9 | 18.3 | 18.9 | 22.9 | 21.3 | 16.7 | 20.1167 | 22.9 | 16.7
2026-05-14 | 19:45:00.000 | 9.8 | 9.8 | 9.8 | 10.1 | 10.1 | 10 | 10.2 | 13.2 | 12.9 | 12.1 | 12.6 | 12.2 | 11.0667 | 13.2 | 9.8 | 9.8 | 10.4 | 10 | 9.6 | 10.9 | 12.1 | 12.4 | 12.9 | 13 | 12.4 | 12.3 | 13.1 | 11.575 | 13.1 | 9.6 | 12 | 11.5 | 10.3 | 11.5 | 11.2 | 9.8 | 10 | 9.9 | 10.1 | 12 | 11.6 | 9 | 10.7417 | 12 | 9
2026-05-14 | 20:00:00.000 | 2.2 | 2.1 | 2.1 | 2.2 | 2.2 | 2.3 | 2.2 | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.4083 | 2.8 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 2.4 | 2.7 | 2.8 | 2.9 | 3 | 2.8 | 2.8 | 3 | 2.5833 | 3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 20:15:00.000 | 0.5 | 0.3 | 0.7 | 0.7 | 0.3 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.8 | 0.8 | 0.70833 | 1 | 0.3 | 0.7 | 0.8 | 0.3 | 0.8 | 0.7 | 1 | 1 | 0.4 | 1.1 | 0.9 | 0.7 | 0.5 | 0.74167 | 1.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 20:30:00.000 | 0.1 | 0.1 | 0.3 | 0.3 | 0.7 | 0.3 | 0.5 | 0.5 | 0.5 | 0.4 | 0.3 | 0.6 | 0.38333 | 0.7 | 0.1 | 0.4 | 0.4 | 0.6 | 0.4 | 0.8 | 0.5 | 0.6 | 0.5 | 0.7 | 0.5 | 0.3 | 0.5 | 0.51667 | 0.8 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.8 | 0.1 | 0.5 | 0.1 | 0.1 | 0.6 | 0.1 | 0.1 | 0.1 | 0.6 | 0.275 | 0.8 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0.2 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0.2 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.13333 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-14 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320