## PR_Calc
PR CALCULATION
15 MAGGIO 2026 | [67 empty] | 15 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 50
RAW PR | [64 empty] | 0.8274 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 82.7398
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 82.6901
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 82.7398
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-15 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5734.1
2026-05-15 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 01:00:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 01:15:00.000 | -1 | -0.00025 | -0.5 | -0.000125 | -0.0001875 | 0 | -0.0001875 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 01:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 01:45:00.000 | -1 | -0.00025 | -0.7 | -0.000175 | -0.0002125 | 0 | -0.0002125 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 02:00:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 02:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 02:30:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 02:45:00.000 | -0.9 | -0.000225 | 0 | 0 | -0.0001125 | 0 | -0.0001125 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 03:00:00.000 | -0.7 | -0.000175 | 0 | 0 | -8.75e-05 | 0 | -8.75e-05 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 03:15:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 03:30:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 03:45:00.000 | -1 | -0.00025 | -0.1 | -2.5e-05 | -0.0001375 | 0 | -0.0001375 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 04:00:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 04:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 04:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 04:45:00.000 | -1 | -0.00025 | -0.7 | -0.000175 | -0.0002125 | 0 | -0.0002125 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 05:00:00.000 | -1 | -0.00025 | -0.2 | -5e-05 | -0.00015 | 0 | -0.00015 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 05:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 05:30:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 06:00:00.000 | 2.1 | 0.000525 | 2.4 | 0.0006 | 0.0005625 | 0 | 0.0005625 | 0.13333 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 06:15:00.000 | 7.2 | 0.0018 | 7.6 | 0.0019 | 0.00185 | 0 | 0.00185 | 0.054054 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 06:30:00.000 | 13.2 | 0.0033 | 13.7 | 0.003425 | 0.0033625 | 0 | 0.0033625 | 0.037175 | 31131.2 | 31131.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 06:45:00.000 | 27.7 | 0.006925 | 28.4 | 0.0071 | 0.0070125 | 0 | 0.0070125 | 0.024955 | 31131.2 | 31131.3 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 07:00:00.000 | 46.4 | 0.0116 | 47.2 | 0.0118 | 0.0117 | 0 | 0.0117 | 0.017094 | 31131.3 | 31131.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 07:15:00.000 | 85.1 | 0.021275 | 86.1 | 0.021525 | 0.0214 | 85.6 | 0.021525 | 0.011682 | 31131.4 | 31131.5 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 07:30:00.000 | 109.2 | 0.0273 | 109.5 | 0.027375 | 0.027338 | 109.35 | 0.027375 | 0.0027435 | 31131.5 | 31131.8 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 07:45:00.000 | 178.2 | 0.04455 | 181.2 | 0.0453 | 0.044925 | 179.7 | 0.0453 | 0.016694 | 31131.8 | 31132.2 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 08:00:00.000 | 245.3 | 0.061325 | 249.5 | 0.062375 | 0.06185 | 247.4 | 0.062375 | 0.016977 | 31132.2 | 31132.7 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 08:15:00.000 | 192.7 | 0.048175 | 194.7 | 0.048675 | 0.048425 | 193.7 | 0.048675 | 0.010325 | 31132.7 | 31133.3 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 08:30:00.000 | 198.9 | 0.049725 | 200.5 | 0.050125 | 0.049925 | 199.7 | 0.050125 | 0.008012 | 31133.3 | 31133.8 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 08:45:00.000 | 131.3 | 0.032825 | 131.6 | 0.0329 | 0.032863 | 131.45 | 0.0329 | 0.0022822 | 31133.8 | 31134.3 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 09:00:00.000 | 118.8 | 0.0297 | 118.2 | 0.02955 | 0.029625 | 118.5 | 0.0297 | 0.0050633 | 31134.3 | 31134.7 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 09:15:00.000 | 134.3 | 0.033575 | 137.3 | 0.034325 | 0.03395 | 135.8 | 0.034325 | 0.022091 | 31134.7 | 31135 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 09:30:00.000 | 306.3 | 0.076575 | 302.2 | 0.07555 | 0.076063 | 304.25 | 0.076575 | 0.013476 | 31135 | 31135.6 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 09:45:00.000 | 381.8 | 0.09545 | 365.3 | 0.091325 | 0.093388 | 373.55 | 0.09545 | 0.044171 | 31135.6 | 31136.5 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 10:00:00.000 | 494.1 | 0.12353 | 460.3 | 0.11507 | 0.1193 | 477.2 | 0.12353 | 0.07083 | 31136.5 | 31137.8 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 10:15:00.000 | 456.2 | 0.11405 | 421.5 | 0.10537 | 0.10971 | 438.85 | 0.11405 | 0.07907 | 31137.8 | 31139 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 10:30:00.000 | 601.8 | 0.15045 | 576.7 | 0.14417 | 0.14731 | 589.25 | 0.15045 | 0.042597 | 31139 | 31140.3 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 10:45:00.000 | 531.3 | 0.13282 | 498.3 | 0.12458 | 0.1287 | 514.8 | 0.13282 | 0.064103 | 31140.3 | 31141.8 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 11:00:00.000 | 557.5 | 0.13937 | 528.8 | 0.1322 | 0.13579 | 543.15 | 0.13937 | 0.05284 | 31141.8 | 31143.2 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 11:15:00.000 | 515.6 | 0.1289 | 504.1 | 0.12602 | 0.12746 | 509.85 | 0.1289 | 0.022556 | 31143.2 | 31144.6 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 11:30:00.000 | 661.2 | 0.1653 | 627.5 | 0.15687 | 0.16109 | 644.35 | 0.1653 | 0.052301 | 31144.6 | 31146.1 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 11:45:00.000 | 879.6 | 0.2199 | 846.7 | 0.21168 | 0.21579 | 863.15 | 0.2199 | 0.038116 | 31146.1 | 31148 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 12:00:00.000 | 788 | 0.197 | 790.2 | 0.19755 | 0.19728 | 789.1 | 0.19755 | 0.002788 | 31148 | 31150.1 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 12:15:00.000 | 771.3 | 0.19282 | 740.7 | 0.18518 | 0.189 | 756 | 0.19282 | 0.040476 | 31150.1 | 31151.8 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 12:30:00.000 | 734.9 | 0.18372 | 717.3 | 0.17932 | 0.18152 | 726.1 | 0.18372 | 0.024239 | 31151.8 | 31153.7 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 12:45:00.000 | 756.9 | 0.18923 | 744.8 | 0.1862 | 0.18771 | 750.85 | 0.18923 | 0.016115 | 31153.7 | 31155.4 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 13:00:00.000 | 813.7 | 0.20343 | 782.9 | 0.19572 | 0.19958 | 798.3 | 0.20343 | 0.038582 | 31155.4 | 31157.4 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 13:15:00.000 | 608.4 | 0.1521 | 588.7 | 0.14718 | 0.14964 | 598.55 | 0.1521 | 0.032913 | 31157.4 | 31159.1 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 13:30:00.000 | 657.2 | 0.1643 | 636.2 | 0.15905 | 0.16168 | 646.7 | 0.1643 | 0.032473 | 31159.1 | 31160.8 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 13:45:00.000 | 573.4 | 0.14335 | 548.7 | 0.13718 | 0.14026 | 561.05 | 0.14335 | 0.044025 | 31160.8 | 31162.4 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 14:00:00.000 | 587.2 | 0.1468 | 574.8 | 0.1437 | 0.14525 | 581 | 0.1468 | 0.021343 | 31162.4 | 31164 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 14:15:00.000 | 535.1 | 0.13378 | 511 | 0.12775 | 0.13076 | 523.05 | 0.13378 | 0.046076 | 31164 | 31165.4 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 14:30:00.000 | 475.1 | 0.11878 | 457.9 | 0.11447 | 0.11663 | 466.5 | 0.11878 | 0.03687 | 31165.4 | 31166.8 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 14:45:00.000 | 395.2 | 0.0988 | 388.2 | 0.09705 | 0.097925 | 391.7 | 0.0988 | 0.017871 | 31166.8 | 31167.9 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 15:00:00.000 | 494.4 | 0.1236 | 478.9 | 0.11972 | 0.12166 | 486.65 | 0.1236 | 0.03185 | 31167.9 | 31169.1 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 15:15:00.000 | 507.8 | 0.12695 | 483.6 | 0.1209 | 0.12393 | 495.7 | 0.12695 | 0.04882 | 31169.1 | 31170.4 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 15:30:00.000 | 494.2 | 0.12355 | 476.5 | 0.11912 | 0.12134 | 485.35 | 0.12355 | 0.036469 | 31170.4 | 31171.8 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 15:45:00.000 | 618.8 | 0.1547 | 602.4 | 0.1506 | 0.15265 | 610.6 | 0.1547 | 0.026859 | 31171.8 | 31173.1 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 16:00:00.000 | 414 | 0.1035 | 375 | 0.09375 | 0.098625 | 394.5 | 0.1035 | 0.098859 | 31173.1 | 31174.5 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 16:15:00.000 | 482.2 | 0.12055 | 448.6 | 0.11215 | 0.11635 | 465.4 | 0.12055 | 0.072196 | 31174.5 | 31175.5 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 16:30:00.000 | 898 | 0.2245 | 882.2 | 0.22055 | 0.22253 | 890.1 | 0.2245 | 0.017751 | 31175.5 | 31177.2 | 1700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 16:45:00.000 | 836.2 | 0.20905 | 767.1 | 0.19178 | 0.20041 | 801.65 | 0.20905 | 0.086197 | 31177.2 | 31179.3 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 17:00:00.000 | 458.7 | 0.11467 | 411.3 | 0.10282 | 0.10875 | 435 | 0.11467 | 0.10897 | 31179.3 | 31180.7 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 17:15:00.000 | 450.5 | 0.11263 | 428.4 | 0.1071 | 0.10986 | 439.45 | 0.11263 | 0.05029 | 31180.7 | 31181.7 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 17:30:00.000 | 471.7 | 0.11793 | 466.7 | 0.11668 | 0.1173 | 469.2 | 0.11793 | 0.010656 | 31181.7 | 31183 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 17:45:00.000 | 406.1 | 0.10153 | 416.1 | 0.10403 | 0.10278 | 411.1 | 0.10403 | 0.024325 | 31183 | 31184.1 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 18:00:00.000 | 235 | 0.05875 | 235.2 | 0.0588 | 0.058775 | 235.1 | 0.0588 | 0.0008507 | 31184.1 | 31184.9 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 18:15:00.000 | 152.9 | 0.038225 | 148.6 | 0.03715 | 0.037687 | 150.75 | 0.038225 | 0.028524 | 31184.9 | 31185.4 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 18:30:00.000 | 110.6 | 0.02765 | 109 | 0.02725 | 0.02745 | 109.8 | 0.02765 | 0.014572 | 31185.4 | 31185.7 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 18:45:00.000 | 121.2 | 0.0303 | 122.5 | 0.030625 | 0.030462 | 121.85 | 0.030625 | 0.010669 | 31185.7 | 31186.1 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 19:00:00.000 | 131.6 | 0.0329 | 152.1 | 0.038025 | 0.035462 | 141.85 | 0.038025 | 0.14452 | 31186.1 | 31186.4 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 19:15:00.000 | 81.8 | 0.02045 | 88.9 | 0.022225 | 0.021338 | 85.35 | 0.022225 | 0.083187 | 31186.4 | 31186.7 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 19:30:00.000 | 55.1 | 0.013775 | 59.1 | 0.014775 | 0.014275 | 57.1 | 0.014775 | 0.070053 | 31186.7 | 31186.9 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 19:45:00.000 | 40.5 | 0.010125 | 46 | 0.0115 | 0.010812 | 0 | 0.010812 | 0.12717 | 31186.9 | 31187 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 20:00:00.000 | 29 | 0.00725 | 29.8 | 0.00745 | 0.00735 | 0 | 0.00735 | 0.027211 | 31187 | 31187.1 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 20:15:00.000 | 11.4 | 0.00285 | 11.6 | 0.0029 | 0.002875 | 0 | 0.002875 | 0.017391 | 31187.1 | 31187.1 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 20:30:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 31187.1 | 31187.2 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 20:45:00.000 | -2 | -0.0005 | -1.9 | -0.000475 | -0.0004875 | 0 | -0.0004875 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 21:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 21:15:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 21:30:00.000 | -1.4 | -0.00035 | -1.4 | -0.00035 | -0.00035 | 0 | -0.00035 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 21:45:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 22:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 22:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 22:30:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 22:45:00.000 | -1 | -0.00025 | -0.6 | -0.00015 | -0.0002 | 0 | -0.0002 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 23:00:00.000 | -0.3 | -7.5e-05 | 0 | 0 | -3.75e-05 | 0 | -3.75e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 23:30:00.000 | -0.9 | -0.000225 | 0 | 0 | -0.0001125 | 0 | -0.0001125 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
2026-05-15 | 23:45:00.000 | -0.3 | -7.5e-05 | 0 | 0 | -3.75e-05 | 0 | -3.75e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96446
PR for each inverter |  |  | 5.5111 |  | 5.3354 | 5.4232 |  | 5.5288 |  |  |  | 56000 |  | 0.7746 | 0.7759 | 0.7868 | 0.79105 | 0.79334 | 0.77183 | 0.78085 | 0.90893 | 0.881 | 0.83277 | 0.86072 | 0.87781 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.7906 | 0.78173 | 0.76943 | 0.77669 | 0.86781 | 0.84819 | 0.89111 | 0.87534 | 0.87157 | 0.87744 | 0.84124 | 0.86893 |  |  |  | 0 | 0.87356 | 0.8544 | 0.78162 | 0.86059 | 0.83794 | 0.77554 | 0.79801 | 0.77334 | 0.7838 | 0.87583 | 0.86103 | 0.79709 | #DIV/0! | #DIV/0! | #DIV/0! | 0 |  | 0.8269 |  | #DIV/0! | #DIV/0! | 1.2047e-05
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-15 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 06:00:00.000 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0
2026-05-15 | 06:15:00.000 | 1.2 | 1.6 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.7 | 1.6 | 1.5 | 1.6 | 1.6 | 1.425 | 1.7 | 1.2 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.7 | 1.7 | 1.6 | 1.7 | 1.6 | 1.6 | 1.7 | 1.4833 | 1.7 | 1.2 | 1.5 | 1.9 | 1.4 | 1.6 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.5 | 1.6 | 1.2 | 1.5083 | 1.9 | 1.2
2026-05-15 | 06:30:00.000 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3 | 3.1 | 4 | 3.9 | 3.6 | 3.8 | 3.8 | 3.4333 | 4 | 3 | 3.2 | 3.3 | 3.1 | 3 | 3.4 | 3.9 | 4 | 3.8 | 3.9 | 3.8 | 3.9 | 4 | 3.6083 | 4 | 3 | 3.8 | 3.9 | 3.4 | 3.9 | 3.7 | 3.6 | 3.5 | 3.5 | 3.4 | 3.9 | 3.8 | 3 | 3.6167 | 3.9 | 3
2026-05-15 | 06:45:00.000 | 7 | 7.1 | 7.1 | 7.2 | 7.1 | 6.9 | 7.1 | 8.9 | 8.7 | 8.2 | 8.6 | 8.5 | 7.7 | 8.9 | 6.9 | 7 | 7.3 | 6.9 | 6.8 | 7.7 | 8.7 | 8.8 | 8.9 | 9 | 8.6 | 8.7 | 9.1 | 8.125 | 9.1 | 6.8 | 8.7 | 8.6 | 7.7 | 8.6 | 8.1 | 7.8 | 7.8 | 7.7 | 7.7 | 8.6 | 8.5 | 6.8 | 8.05 | 8.7 | 6.8
2026-05-15 | 07:00:00.000 | 11.9 | 12.1 | 12.1 | 12.3 | 12.2 | 11.8 | 12.1 | 15.2 | 14.8 | 14 | 14.8 | 14.5 | 13.15 | 15.2 | 11.8 | 12 | 12.1 | 12 | 11.7 | 13.2 | 14.8 | 14.9 | 15.4 | 15.3 | 14.7 | 14.8 | 15.5 | 13.8667 | 15.5 | 11.7 | 14.9 | 14.7 | 13.1 | 14.6 | 14.2 | 13.2 | 13.2 | 13 | 13 | 14.8 | 14.5 | 11.5 | 13.725 | 14.9 | 11.5
2026-05-15 | 07:15:00.000 | 21.9 | 22 | 22.1 | 22.6 | 22.5 | 21.8 | 22.2 | 27.9 | 27.3 | 25.8 | 27.2 | 26.5 | 24.15 | 27.9 | 21.8 | 22 | 22.9 | 22.3 | 20.8 | 24.4 | 27.2 | 27.4 | 28.3 | 28.3 | 27.1 | 27 | 28.4 | 25.5083 | 28.4 | 20.8 | 27.4 | 26.8 | 24 | 26.9 | 26 | 23.9 | 23.9 | 23.5 | 23.6 | 27 | 26.5 | 21.1 | 25.05 | 27.4 | 21.1
2026-05-15 | 07:30:00.000 | 28.2 | 28.3 | 28.5 | 29.1 | 29 | 28.4 | 28.7 | 35.9 | 35.1 | 32.1 | 35 | 33.9 | 31.0167 | 35.9 | 28.2 | 28.3 | 29.4 | 28.8 | 27.8 | 31.5 | 34.8 | 35.2 | 36.4 | 36.6 | 34.8 | 34.5 | 36.5 | 32.8833 | 36.6 | 27.8 | 35.5 | 34.3 | 31 | 34.6 | 33.7 | 30.4 | 30.7 | 30.1 | 30.2 | 34.9 | 34.3 | 27.2 | 32.2417 | 35.5 | 27.2
2026-05-15 | 07:45:00.000 | 44.6 | 44.9 | 45.5 | 46.5 | 46.2 | 43.8 | 46.5 | 57.7 | 56.3 | 52.9 | 56.2 | 54.7 | 49.65 | 57.7 | 43.8 | 45.8 | 46.7 | 46.8 | 44.7 | 50.8 | 56.2 | 54.3 | 59.2 | 59.6 | 56.4 | 55 | 58.4 | 52.825 | 59.6 | 44.7 | 57.1 | 54.1 | 49 | 55.3 | 53.5 | 47.6 | 48.6 | 47.2 | 47.7 | 53.2 | 54.6 | 43 | 50.9083 | 57.1 | 43
2026-05-15 | 08:00:00.000 | 63.3 | 63.5 | 63.6 | 65.3 | 65.7 | 63.1 | 64.1 | 80.2 | 76 | 74.9 | 78.7 | 76.4 | 69.5667 | 80.2 | 63.1 | 63.3 | 65.6 | 63.8 | 62.8 | 70.9 | 78.9 | 79.8 | 82 | 81.9 | 77.4 | 76.4 | 77.9 | 73.3917 | 82 | 62.8 | 80.2 | 77 | 69.9 | 78.6 | 76.2 | 68.2 | 66.9 | 66.5 | 67.3 | 78.5 | 77.7 | 58.9 | 72.1583 | 80.2 | 58.9
2026-05-15 | 08:15:00.000 | 50.8 | 50.6 | 50.9 | 52.4 | 52 | 48.9 | 51.6 | 62.3 | 62.8 | 59.3 | 62.3 | 61 | 55.4083 | 62.8 | 48.9 | 50.5 | 52.4 | 51.1 | 49.5 | 55.7 | 62.6 | 63.7 | 65.1 | 64.9 | 61.5 | 60.3 | 64.2 | 58.4583 | 65.1 | 49.5 | 63.1 | 61.9 | 55.3 | 62.5 | 61 | 54.4 | 55.5 | 53.3 | 53.4 | 62.2 | 61.5 | 48.1 | 57.6833 | 63.1 | 48.1
2026-05-15 | 08:30:00.000 | 53.2 | 52.7 | 53.1 | 54.5 | 54.2 | 53 | 54.1 | 67.7 | 65.2 | 61.7 | 65 | 63.3 | 58.1417 | 67.7 | 52.7 | 53.3 | 53.3 | 54 | 51.6 | 58.1 | 65.6 | 65.6 | 67.7 | 67.1 | 63.4 | 62.2 | 66.1 | 60.6667 | 67.7 | 51.6 | 62.9 | 64.4 | 57.8 | 64.6 | 63.5 | 56.7 | 57.7 | 55.5 | 56 | 65.2 | 63.4 | 51.3 | 59.9167 | 65.2 | 51.3
2026-05-15 | 08:45:00.000 | 36.6 | 36.4 | 36.7 | 37.9 | 37.9 | 37.3 | 38.5 | 47.2 | 45.8 | 43.4 | 45.6 | 44.8 | 40.675 | 47.2 | 36.4 | 38.1 | 39.8 | 38.9 | 35.8 | 42.1 | 46.6 | 43.1 | 48.6 | 48.2 | 45.9 | 45.2 | 48.3 | 43.3833 | 48.6 | 35.8 | 45.5 | 44.6 | 40 | 43.9 | 43.1 | 38.5 | 39.1 | 37.7 | 38.2 | 44.5 | 43.4 | 34 | 41.0417 | 45.5 | 34
2026-05-15 | 09:00:00.000 | 36 | 35.3 | 35.2 | 36 | 35.9 | 35.1 | 36 | 44.5 | 42.7 | 40.4 | 42 | 41.3 | 38.3667 | 44.5 | 35.1 | 35.7 | 36.9 | 35.9 | 34.2 | 38.5 | 42.7 | 42.4 | 44 | 43.4 | 41.1 | 40.6 | 43.1 | 39.875 | 44 | 34.2 | 42.5 | 42 | 38.3 | 41.8 | 41.3 | 37.7 | 38.6 | 37 | 37.3 | 42.5 | 41.5 | 34.4 | 39.575 | 42.5 | 34.4
2026-05-15 | 09:15:00.000 | 40.1 | 39.4 | 39.1 | 40.3 | 40.8 | 39 | 40 | 48 | 47.3 | 45.8 | 47.3 | 45.7 | 42.7333 | 48 | 39 | 39.5 | 40.7 | 39.6 | 37.6 | 42.1 | 45.9 | 46.6 | 48.5 | 47.7 | 45.1 | 44.4 | 47.1 | 43.7333 | 48.5 | 37.6 | 47.5 | 47.3 | 43.3 | 46.9 | 45.9 | 41.5 | 43 | 41.1 | 40 | 47.4 | 47.1 | 37 | 44 | 47.5 | 37
2026-05-15 | 09:30:00.000 | 87.7 | 82.6 | 90.1 | 77.8 | 82.5 | 83.8 | 84.3 | 110 | 102 | 90.9 | 94.9 | 93.4 | 90 | 110 | 77.8 | 83.9 | 86.7 | 84.8 | 79.8 | 89.9 | 95.6 | 98.5 | 95.2 | 99 | 95.3 | 94.3 | 98.4 | 91.7833 | 99 | 79.8 | 102.5 | 100.7 | 94.7 | 104.8 | 103.4 | 93.9 | 99 | 93.4 | 89.4 | 105.5 | 99.9 | 88.6 | 97.9833 | 105.5 | 88.6
2026-05-15 | 09:45:00.000 | 104.9 | 102.2 | 101.4 | 101.7 | 103.3 | 100.3 | 101.7 | 132.3 | 120.7 | 112.1 | 116 | 112.4 | 109.0833 | 132.3 | 100.3 | 100.1 | 102.7 | 103.6 | 94 | 105 | 114.6 | 114.2 | 116.2 | 113.9 | 108.3 | 113.3 | 110.2 | 108.0083 | 116.2 | 94 | 116.7 | 115.4 | 107.1 | 119.5 | 118.1 | 108.6 | 115.3 | 108.4 | 106.4 | 117.6 | 114.3 | 106.1 | 112.7917 | 119.5 | 106.1
2026-05-15 | 10:00:00.000 | 144.3 | 139.4 | 153.8 | 151.7 | 158.2 | 145.9 | 156.8 | 182.2 | 178.6 | 164.5 | 177.2 | 170.6 | 160.2667 | 182.2 | 139.4 | 150.6 | 150.1 | 157.7 | 145.2 | 161.3 | 169.7 | 168.3 | 174.9 | 172.8 | 165.3 | 169 | 173.9 | 163.2333 | 174.9 | 145.2 | 160.5 | 153.8 | 133.7 | 149.8 | 147.2 | 131.9 | 141 | 137.7 | 136.7 | 157.2 | 160.6 | 133.9 | 145.3333 | 160.6 | 131.9
2026-05-15 | 10:15:00.000 | 122.3 | 124 | 128.5 | 128.7 | 122.9 | 125.1 | 126.4 | 149.6 | 145.2 | 133.6 | 136.3 | 134.1 | 131.3917 | 149.6 | 122.3 | 116.8 | 117 | 115.7 | 110.1 | 127.9 | 132.3 | 140.8 | 137.3 | 134 | 137.9 | 142.2 | 133.2 | 128.7667 | 142.2 | 110.1 | 137.6 | 131.9 | 117.6 | 132.2 | 119.5 | 115.3 | 119.4 | 105.6 | 126.8 | 130.8 | 136.6 | 113.3 | 123.8833 | 137.6 | 105.6
2026-05-15 | 10:30:00.000 | 159 | 160.1 | 160 | 170.1 | 162 | 149.2 | 156.9 | 188.3 | 180.4 | 173.6 | 180 | 158.6 | 166.5167 | 188.3 | 149.2 | 136.7 | 140.7 | 141.9 | 135.1 | 149.8 | 168.4 | 169.1 | 166.2 | 169.6 | 156.3 | 164.5 | 164.2 | 155.2083 | 169.6 | 135.1 | 170.7 | 167.4 | 167.5 | 180 | 175.9 | 153.4 | 153.4 | 160.6 | 158.1 | 180.1 | 180.6 | 150.1 | 166.4833 | 180.6 | 150.1
2026-05-15 | 10:45:00.000 | 138.6 | 142.4 | 149.4 | 141.5 | 146.1 | 146.3 | 150.9 | 176.4 | 161.5 | 156 | 156.6 | 159 | 152.0583 | 176.4 | 138.6 | 127.2 | 138 | 135.6 | 132.4 | 148.2 | 160.7 | 160.4 | 163.3 | 162 | 150 | 156 | 160.2 | 149.5 | 163.3 | 127.2 | 154.1 | 153.1 | 141 | 159 | 157.9 | 143.9 | 156.5 | 145.9 | 148.2 | 165.8 | 158.9 | 149.5 | 152.8167 | 165.8 | 141
2026-05-15 | 11:00:00.000 | 146.5 | 144.6 | 156.7 | 156.3 | 160.4 | 165.4 | 170.9 | 181.5 | 175.6 | 168.2 | 172.2 | 180.9 | 164.9333 | 181.5 | 144.6 | 152 | 149.4 | 162.1 | 155 | 167.1 | 172 | 174.3 | 176.7 | 176.7 | 176.6 | 180.5 | 183.6 | 168.8333 | 183.6 | 149.4 | 169.1 | 162.5 | 142 | 157.5 | 157.9 | 155 | 161.7 | 152.8 | 153.1 | 173.4 | 170.6 | 138.8 | 157.8667 | 173.4 | 138.8
2026-05-15 | 11:15:00.000 | 132.4 | 140.5 | 148.2 | 153.5 | 143.1 | 151.6 | 159.5 | 176.5 | 180.7 | 172.5 | 169.1 | 177.8 | 158.7833 | 180.7 | 132.4 | 149.4 | 153.1 | 153 | 146.2 | 159.2 | 145.1 | 177 | 175.1 | 167.4 | 163.1 | 166.7 | 173.9 | 160.7667 | 177 | 145.1 | 178.9 | 156.9 | 142.8 | 161 | 160.3 | 139.5 | 141.5 | 146.4 | 156 | 169.5 | 161.5 | 120.9 | 152.9333 | 178.9 | 120.9
2026-05-15 | 11:30:00.000 | 173.9 | 173.5 | 175.8 | 181.3 | 183.3 | 175.9 | 171.8 | 212.1 | 208.3 | 183.7 | 201.2 | 197.4 | 186.5167 | 212.1 | 171.8 | 160.2 | 173.9 | 169.9 | 164.1 | 177.8 | 201.7 | 193.4 | 198.5 | 197.8 | 179.6 | 185 | 192.8 | 182.8917 | 201.7 | 160.2 | 190.4 | 203.3 | 169.3 | 190.3 | 180.6 | 172.5 | 176.5 | 168.6 | 175.9 | 189.6 | 194.4 | 147 | 179.8667 | 203.3 | 147
2026-05-15 | 11:45:00.000 | 226.5 | 219.6 | 220.7 | 218.7 | 225.7 | 209 | 202.2 | 246 | 236.8 | 228.6 | 231.2 | 227.7 | 224.3917 | 246 | 202.2 | 190.5 | 205.9 | 192.4 | 187.8 | 197.9 | 219 | 226.9 | 227.2 | 224.1 | 207.9 | 211.1 | 203.5 | 207.85 | 227.2 | 187.8 | 239.2 | 244.3 | 228.5 | 229.8 | 211.6 | 219.6 | 210.6 | 218 | 232.8 | 244.4 | 223.2 | 193.5 | 224.625 | 244.4 | 193.5
2026-05-15 | 12:00:00.000 | 198.5 | 200.2 | 213.6 | 211.5 | 215.8 | 208.7 | 216.7 | 245.2 | 233 | 238.2 | 232.6 | 235.1 | 220.7583 | 245.2 | 198.5 | 206.8 | 221.1 | 231.6 | 218.1 | 240.1 | 241.7 | 242.5 | 250.2 | 249.7 | 249 | 248.8 | 249 | 237.3833 | 250.2 | 206.8 | 236.4 | 240.2 | 226.1 | 239 | 233.9 | 221.9 | 225.8 | 205.4 | 219.3 | 232.1 | 231.1 | 206.3 | 226.4583 | 240.2 | 205.4
2026-05-15 | 12:15:00.000 | 188.3 | 190.8 | 190.6 | 183.2 | 184.1 | 177.2 | 174.1 | 219.8 | 207.2 | 196.8 | 200.9 | 184.5 | 191.4583 | 219.8 | 174.1 | 169.9 | 174.1 | 158.8 | 172.6 | 187.9 | 190.3 | 193.6 | 187.5 | 192.3 | 185.4 | 190.4 | 200.1 | 183.575 | 200.1 | 158.8 | 206.5 | 201.6 | 195.5 | 222.3 | 204 | 204 | 209.2 | 210.1 | 203.7 | 217.3 | 207.9 | 195.9 | 206.5 | 222.3 | 195.5
2026-05-15 | 12:30:00.000 | 174.1 | 181.2 | 177.5 | 181.8 | 184.8 | 179.9 | 179 | 217.2 | 207.5 | 195.4 | 199.7 | 199.8 | 189.825 | 217.2 | 174.1 | 173.6 | 181.6 | 179 | 167.8 | 180.2 | 199.7 | 203.9 | 203.8 | 201.5 | 193.1 | 199 | 196.3 | 189.9583 | 203.9 | 167.8 | 200 | 216.1 | 198.2 | 202.6 | 206.9 | 181.2 | 200.1 | 200.9 | 202 | 217.7 | 207.8 | 191.9 | 202.1167 | 217.7 | 181.2
2026-05-15 | 12:45:00.000 | 186.7 | 190.7 | 203.4 | 199.7 | 192.3 | 193.5 | 183.1 | 227 | 221.9 | 208.2 | 212.2 | 209.4 | 202.3417 | 227 | 183.1 | 184.4 | 192.4 | 184.5 | 168.6 | 194.6 | 193.2 | 208.5 | 206.6 | 205.8 | 201.4 | 209.2 | 209.6 | 196.5667 | 209.6 | 168.6 | 215.5 | 222.5 | 209.5 | 225.1 | 212.1 | 207.7 | 207.2 | 204.8 | 206.6 | 218.1 | 221.8 | 191 | 211.825 | 225.1 | 191
2026-05-15 | 13:00:00.000 | 215.5 | 214.3 | 210.5 | 207.4 | 213.3 | 211.1 | 208.3 | 241.9 | 243.4 | 230 | 227.1 | 234.2 | 221.4167 | 243.4 | 207.4 | 208.4 | 215.9 | 200.6 | 206.2 | 225.7 | 238 | 237.6 | 244.9 | 244.1 | 235.2 | 219.6 | 240 | 226.35 | 244.9 | 200.6 | 240 | 227.6 | 219.4 | 242.1 | 229.5 | 222.9 | 229.9 | 213.7 | 220.3 | 247.8 | 233.8 | 213.4 | 228.3667 | 247.8 | 213.4
2026-05-15 | 13:15:00.000 | 160.9 | 162.5 | 160 | 166.6 | 165.4 | 159 | 161.6 | 201.5 | 193.6 | 179.7 | 192.5 | 187.6 | 174.2417 | 201.5 | 159 | 157.4 | 163.7 | 161.6 | 153.7 | 172.8 | 192.6 | 190.2 | 197 | 197.2 | 187.2 | 187.9 | 194.7 | 179.6667 | 197.2 | 153.7 | 201.3 | 187 | 173.9 | 191.8 | 183 | 170.2 | 168.9 | 168.6 | 165.9 | 197.6 | 192.3 | 157.8 | 179.8583 | 201.3 | 157.8
2026-05-15 | 13:30:00.000 | 171.9 | 171.2 | 177.6 | 175 | 179.5 | 175.9 | 179 | 220.4 | 215.1 | 191.9 | 210.8 | 204.1 | 189.3667 | 220.4 | 171.2 | 176.9 | 183.4 | 178.4 | 174.9 | 196.4 | 214.6 | 217.4 | 221.4 | 216.9 | 215.3 | 205.6 | 224.3 | 202.125 | 224.3 | 174.9 | 210.5 | 210.9 | 179.9 | 210 | 205.3 | 186 | 188.3 | 182.3 | 181 | 215.5 | 200.2 | 166.5 | 194.7 | 215.5 | 166.5
2026-05-15 | 13:45:00.000 | 153.6 | 153.3 | 155.3 | 155.1 | 154.3 | 150.4 | 150.9 | 190.6 | 183 | 173.8 | 180.2 | 174.2 | 164.5583 | 190.6 | 150.4 | 148.2 | 153.1 | 148.8 | 144.4 | 162.2 | 179.1 | 178.1 | 183.8 | 183.8 | 176.3 | 176.1 | 183.4 | 168.1083 | 183.8 | 144.4 | 184.8 | 179.3 | 164.4 | 176.4 | 178.1 | 162.1 | 167.8 | 161.1 | 163.2 | 185.7 | 181.3 | 148.1 | 171.025 | 185.7 | 148.1
2026-05-15 | 14:00:00.000 | 157.2 | 157.6 | 157.2 | 160.7 | 161.5 | 157 | 161.1 | 197.9 | 195.3 | 186.1 | 193 | 185.6 | 172.5167 | 197.9 | 157 | 157.7 | 163.4 | 159.2 | 153.8 | 173.4 | 194.3 | 190.3 | 198.7 | 198.5 | 187.8 | 181.1 | 194.8 | 179.4167 | 198.7 | 153.8 | 200.7 | 186.2 | 173.4 | 183.5 | 183.5 | 167.7 | 167 | 165.2 | 166.7 | 192.4 | 190.4 | 144.7 | 176.7833 | 200.7 | 144.7
2026-05-15 | 14:15:00.000 | 143.1 | 141.7 | 144.2 | 143.8 | 142.5 | 140.2 | 140.5 | 175.4 | 166.5 | 161.6 | 168.4 | 163.9 | 152.65 | 175.4 | 140.2 | 134.7 | 145.1 | 141 | 137.4 | 156.1 | 170.2 | 171.5 | 178.8 | 179.3 | 171.5 | 169.5 | 180.5 | 161.3 | 180.5 | 134.7 | 174.9 | 170.3 | 153.3 | 163.9 | 169 | 149.7 | 155.1 | 150.6 | 151.7 | 171.3 | 163.7 | 141.2 | 159.5583 | 174.9 | 141.2
2026-05-15 | 14:30:00.000 | 127.6 | 127.7 | 124 | 127.4 | 119.9 | 120.7 | 119.3 | 153.4 | 147.2 | 134.5 | 146.8 | 140.2 | 132.3917 | 153.4 | 119.3 | 116.8 | 120.7 | 116.9 | 114.8 | 128.6 | 143.8 | 141.4 | 148.1 | 146.3 | 138.6 | 139.8 | 137.7 | 132.7917 | 148.1 | 114.8 | 151.6 | 149 | 135.3 | 152.5 | 151.3 | 137.8 | 141.2 | 136.2 | 136 | 152.8 | 145 | 134.2 | 143.575 | 152.8 | 134.2
2026-05-15 | 14:45:00.000 | 106.1 | 106.3 | 107.5 | 108.3 | 107.9 | 106.3 | 107.3 | 133.6 | 131.3 | 124.8 | 123.9 | 126.1 | 115.7833 | 133.6 | 106.1 | 106.5 | 109.1 | 107.8 | 101.2 | 119 | 131 | 130.3 | 137.1 | 137 | 131.2 | 130.2 | 136.9 | 123.1083 | 137.1 | 101.2 | 136 | 129.5 | 116.3 | 130.3 | 126.5 | 115.3 | 118.2 | 112.5 | 113.2 | 125.8 | 130.4 | 105.9 | 121.6583 | 136 | 105.9
2026-05-15 | 15:00:00.000 | 131 | 127.3 | 132.5 | 135.1 | 134.1 | 131.6 | 132.1 | 164.4 | 160 | 152.5 | 158.6 | 151.5 | 142.5583 | 164.4 | 127.3 | 130.6 | 133.3 | 130.5 | 126 | 142.2 | 154.3 | 155.3 | 161.5 | 162.2 | 155.6 | 153.8 | 158 | 146.9417 | 162.2 | 126 | 162 | 149.7 | 141.2 | 157.3 | 153.9 | 140.1 | 142.9 | 138.6 | 139.6 | 160.5 | 152.4 | 131 | 147.4333 | 162 | 131
2026-05-15 | 15:15:00.000 | 131.1 | 136.2 | 135 | 137.4 | 136 | 132.2 | 132.6 | 161.5 | 162.1 | 151.5 | 152.8 | 147.5 | 142.9917 | 162.1 | 131.1 | 130.3 | 133.6 | 132.6 | 127.8 | 144 | 157.9 | 156.1 | 161.6 | 162.1 | 154.9 | 155.2 | 161.5 | 148.1333 | 162.1 | 127.8 | 164.3 | 157.9 | 143.3 | 160.3 | 156.5 | 142.4 | 147.5 | 142.2 | 143.2 | 163.4 | 160.6 | 127.9 | 150.7917 | 164.3 | 127.9
2026-05-15 | 15:30:00.000 | 132.1 | 133 | 128.4 | 135.1 | 135.3 | 132.3 | 128.5 | 165.9 | 161.5 | 147.5 | 159.7 | 149.6 | 142.4083 | 165.9 | 128.4 | 132.1 | 135.4 | 134.5 | 129.5 | 146.2 | 159.1 | 157.9 | 165.4 | 165.6 | 158.8 | 158.5 | 166.3 | 150.775 | 166.3 | 129.5 | 164.3 | 158.1 | 138.5 | 160 | 155.1 | 141.1 | 143.2 | 138.7 | 139.8 | 159.7 | 159.3 | 127.4 | 148.7667 | 164.3 | 127.4
2026-05-15 | 15:45:00.000 | 159.7 | 159.6 | 155.7 | 157.4 | 164.9 | 155.7 | 161.2 | 196.3 | 195.6 | 186.7 | 192.9 | 187.7 | 172.7833 | 196.3 | 155.7 | 164.8 | 167.2 | 165.3 | 160.5 | 179.4 | 196 | 183.4 | 202 | 192.6 | 192.4 | 193.1 | 202.1 | 183.2333 | 202.1 | 160.5 | 196.9 | 191.4 | 174.8 | 188.8 | 170.6 | 165 | 170.6 | 166 | 170.5 | 194.3 | 189.7 | 153.3 | 177.6583 | 196.9 | 153.3
2026-05-15 | 16:00:00.000 | 111.9 | 110 | 110.4 | 110.3 | 109.9 | 106.3 | 104.1 | 132.7 | 127.9 | 118.3 | 123.2 | 116.7 | 115.1417 | 132.7 | 104.1 | 101.1 | 102.3 | 100.4 | 97.1 | 109.8 | 118.2 | 118.4 | 122.3 | 122.9 | 117.6 | 117.9 | 123.2 | 112.6 | 123.2 | 97.1 | 125.3 | 120.8 | 110.1 | 123.7 | 121.7 | 111.5 | 119.7 | 114.7 | 109.2 | 128.3 | 126.9 | 112.6 | 118.7083 | 128.3 | 109.2
2026-05-15 | 16:15:00.000 | 117 | 116.4 | 120.5 | 118.7 | 116.8 | 115.2 | 119.4 | 135.4 | 138.6 | 136.4 | 138.6 | 136.1 | 125.7583 | 138.6 | 115.2 | 112.3 | 119.9 | 117.3 | 114.1 | 130.7 | 135.6 | 131.9 | 140.4 | 140.6 | 134.4 | 134.2 | 136.7 | 129.0083 | 140.6 | 112.3 | 141.5 | 133.4 | 122.3 | 135.4 | 135 | 127 | 130.2 | 114.9 | 127.3 | 139 | 139.1 | 122 | 130.5917 | 141.5 | 114.9
2026-05-15 | 16:30:00.000 | 224.5 | 221 | 222.5 | 226.1 | 234.4 | 218.7 | 222.6 | 252.7 | 245.1 | 242.1 | 242.5 | 233.7 | 232.1583 | 252.7 | 218.7 | 218.5 | 227.7 | 223 | 214.5 | 232.8 | 234.9 | 224.6 | 234.2 | 232.8 | 233.7 | 233.3 | 236.4 | 228.8667 | 236.4 | 214.5 | 233.8 | 238.8 | 232.1 | 248.4 | 247 | 232.4 | 231.8 | 234.3 | 231.1 | 239.5 | 246.9 | 244.3 | 238.3667 | 248.4 | 231.1
2026-05-15 | 16:45:00.000 | 208.6 | 207.6 | 206.9 | 204.7 | 201 | 190.6 | 193.6 | 245.2 | 229.8 | 214 | 217.3 | 204.6 | 210.325 | 245.2 | 190.6 | 180.5 | 186.2 | 183.2 | 177.2 | 195.1 | 201.5 | 202.6 | 207.5 | 206.1 | 199.6 | 198.3 | 202 | 194.9833 | 207.5 | 177.2 | 217.9 | 220.2 | 203.2 | 232.3 | 232 | 218.3 | 228.6 | 220.9 | 221.9 | 234.1 | 233.9 | 221.1 | 223.7 | 234.1 | 203.2
2026-05-15 | 17:00:00.000 | 110.4 | 114 | 114.3 | 116.1 | 118.4 | 116.5 | 119.4 | 141.2 | 136.9 | 130.5 | 135.7 | 132.1 | 123.7917 | 141.2 | 110.4 | 115.7 | 120 | 117.6 | 115.6 | 130.6 | 131.2 | 127 | 124.4 | 125.8 | 128 | 131.5 | 134.1 | 125.125 | 134.1 | 115.6 | 125.7 | 122.1 | 111.4 | 123.1 | 119.4 | 111.4 | 119.9 | 114.6 | 116.6 | 133.7 | 131.6 | 93.7 | 118.6 | 133.7 | 93.7
2026-05-15 | 17:15:00.000 | 110.8 | 112.6 | 110 | 113.3 | 111.2 | 109 | 111.6 | 138.8 | 133.9 | 127.3 | 132.5 | 132.4 | 120.2833 | 138.8 | 109 | 111.5 | 112.8 | 112.9 | 107.9 | 124.4 | 136.3 | 133.5 | 141.3 | 141.6 | 136.4 | 137.8 | 145.3 | 128.475 | 145.3 | 107.9 | 139.8 | 135.5 | 118.9 | 132.6 | 130.6 | 112.9 | 123.3 | 116.4 | 116.5 | 132.8 | 138 | 107.6 | 125.4083 | 139.8 | 107.6
2026-05-15 | 17:30:00.000 | 118.7 | 119.7 | 120.6 | 121.3 | 122.1 | 118.8 | 121.2 | 152.9 | 148.8 | 140.3 | 146.3 | 140.8 | 130.9583 | 152.9 | 118.7 | 118.9 | 122.2 | 120.4 | 116.3 | 133 | 145 | 144.1 | 150.5 | 148 | 145.1 | 144.2 | 151.8 | 136.625 | 151.8 | 116.3 | 153.4 | 146.9 | 131.1 | 146.6 | 143.2 | 129.5 | 134.6 | 129.5 | 130.8 | 147.7 | 149.7 | 119.1 | 138.5083 | 153.4 | 119.1
2026-05-15 | 17:45:00.000 | 102.2 | 103.3 | 103.8 | 104.8 | 104.6 | 102.4 | 104.9 | 133.2 | 130.1 | 121 | 127.3 | 122.5 | 113.3417 | 133.2 | 102.2 | 102.1 | 104.8 | 104 | 100.1 | 114.3 | 119.8 | 125.5 | 130.7 | 132.6 | 126.5 | 125.2 | 132.3 | 118.1583 | 132.6 | 100.1 | 134.1 | 128.2 | 113.5 | 126.6 | 123.4 | 110.5 | 115.8 | 111.9 | 107.7 | 126.9 | 130.1 | 102.6 | 119.275 | 134.1 | 102.6
2026-05-15 | 18:00:00.000 | 62 | 62.4 | 62.1 | 63.4 | 63.8 | 61.5 | 62.5 | 79.2 | 76.9 | 72.7 | 75.9 | 73.3 | 67.975 | 79.2 | 61.5 | 61.9 | 64 | 62.8 | 58.7 | 69.2 | 74.8 | 75.4 | 78.2 | 78.8 | 75.6 | 74.2 | 78.6 | 71.0167 | 78.8 | 58.7 | 78.6 | 74.2 | 67.4 | 74.3 | 72 | 64.1 | 67.3 | 65.4 | 64.5 | 75 | 75.6 | 60.9 | 69.9417 | 78.6 | 60.9
2026-05-15 | 18:15:00.000 | 40.8 | 40.9 | 41.1 | 41.8 | 42 | 40.9 | 41.1 | 51.8 | 50.5 | 47.9 | 50.1 | 48.4 | 44.775 | 51.8 | 40.8 | 41 | 42.2 | 41.5 | 40.2 | 45.7 | 50.2 | 50.7 | 52.8 | 53 | 50.7 | 50.2 | 53.1 | 47.6083 | 53.1 | 40.2 | 51.1 | 48.7 | 42.5 | 49.1 | 48 | 42.3 | 44.1 | 42.7 | 43.1 | 49.5 | 49.3 | 39.3 | 45.8083 | 51.1 | 39.3
2026-05-15 | 18:30:00.000 | 29.7 | 29.8 | 29.9 | 30.5 | 30.6 | 29.8 | 30 | 37.8 | 37 | 35.1 | 36.7 | 35.4 | 32.6917 | 37.8 | 29.7 | 29.9 | 30.9 | 30.3 | 29.4 | 33.4 | 36.8 | 37.2 | 38.7 | 38.9 | 37.1 | 36.6 | 38.9 | 34.8417 | 38.9 | 29.4 | 37.4 | 35.6 | 32.1 | 36 | 35.1 | 31.5 | 32.2 | 31.2 | 31.6 | 36.3 | 36.1 | 28.6 | 33.6417 | 37.4 | 28.6
2026-05-15 | 18:45:00.000 | 32.4 | 32.5 | 32.7 | 33.3 | 33.3 | 32.5 | 32.9 | 41.5 | 40.6 | 38.5 | 40.3 | 38.9 | 35.7833 | 41.5 | 32.4 | 32.6 | 33.7 | 33.1 | 31.9 | 36.3 | 40 | 40.5 | 42 | 42.2 | 40.2 | 39.6 | 42 | 37.8417 | 42.2 | 31.9 | 41.2 | 39.5 | 35.5 | 39.8 | 38.7 | 34.6 | 35.3 | 34.3 | 34.8 | 40.3 | 39.8 | 31.4 | 37.1 | 41.2 | 31.4
2026-05-15 | 19:00:00.000 | 34.5 | 34.7 | 34.4 | 35.1 | 35.6 | 34 | 34 | 45.9 | 44.4 | 42.5 | 44.6 | 41.8 | 38.4583 | 45.9 | 34 | 34.4 | 35.5 | 35 | 32.8 | 37.9 | 42.5 | 42.4 | 44.6 | 44.3 | 41.5 | 39.7 | 42.6 | 39.4333 | 44.6 | 32.8 | 47.5 | 45.3 | 40.5 | 44.5 | 43 | 38.5 | 39.4 | 38.1 | 39.5 | 47.6 | 44.8 | 34.9 | 41.9667 | 47.6 | 34.9
2026-05-15 | 19:15:00.000 | 22.1 | 22.2 | 22.2 | 22.8 | 22.8 | 22.3 | 22.9 | 29.1 | 28.5 | 26.8 | 28.2 | 27.2 | 24.7583 | 29.1 | 22.1 | 22.3 | 23.3 | 22.7 | 21.6 | 24.7 | 27.4 | 27.7 | 28.7 | 28.7 | 27.2 | 26.7 | 28.4 | 25.7833 | 28.7 | 21.6 | 29 | 28.2 | 25.2 | 28.1 | 27.3 | 24 | 24.7 | 24 | 24.6 | 29 | 28.2 | 21.9 | 26.1833 | 29 | 21.9
2026-05-15 | 19:30:00.000 | 14.8 | 14.8 | 14.8 | 15.3 | 15.3 | 15 | 15.3 | 19.5 | 19 | 18 | 18.9 | 18.1 | 16.5667 | 19.5 | 14.8 | 14.8 | 15.5 | 15.1 | 14.4 | 16.4 | 18.2 | 18.5 | 19.1 | 19.1 | 18.1 | 17.8 | 19 | 17.1667 | 19.1 | 14.4 | 19.3 | 18.6 | 16.8 | 18.6 | 18.1 | 15.9 | 16.4 | 16 | 16.4 | 19.3 | 18.7 | 14.6 | 17.3917 | 19.3 | 14.6
2026-05-15 | 19:45:00.000 | 11 | 11 | 11 | 11.3 | 11.3 | 11.1 | 11.5 | 14.8 | 14.5 | 13.6 | 14.2 | 13.7 | 12.4167 | 14.8 | 11 | 11 | 11.6 | 11.3 | 10.7 | 12.2 | 13.6 | 14.1 | 14.7 | 14.7 | 14.2 | 14.1 | 15.1 | 13.1083 | 15.1 | 10.7 | 14.6 | 14.3 | 12.8 | 14.2 | 13.8 | 12.1 | 12.6 | 12.2 | 12.6 | 14.9 | 14.2 | 11.2 | 13.2917 | 14.9 | 11.2
2026-05-15 | 20:00:00.000 | 7.8 | 7.8 | 7.8 | 8 | 8.1 | 7.9 | 7.8 | 10 | 9.7 | 9.2 | 9.5 | 9.2 | 8.5667 | 10 | 7.8 | 7.9 | 8.2 | 8 | 7.7 | 8.8 | 9.5 | 9.7 | 10.1 | 10.2 | 9.7 | 9.6 | 10.2 | 9.1333 | 10.2 | 7.7 | 9.4 | 9.1 | 8.3 | 9.1 | 9 | 8 | 8.3 | 8.1 | 8.3 | 9.6 | 9.2 | 7.4 | 8.65 | 9.6 | 7.4
2026-05-15 | 20:15:00.000 | 3.1 | 3 | 3.1 | 3.2 | 3.2 | 3.2 | 3.2 | 4 | 3.9 | 3.8 | 3.9 | 3.7 | 3.4417 | 4 | 3 | 3.1 | 3.3 | 3.2 | 3 | 3.4 | 3.8 | 3.9 | 4 | 4.1 | 3.9 | 3.9 | 4.1 | 3.6417 | 4.1 | 3 | 3.9 | 3.6 | 3.4 | 3.7 | 3.7 | 3.2 | 3.3 | 3.3 | 3.4 | 3.9 | 3.8 | 3 | 3.5167 | 3.9 | 3
2026-05-15 | 20:30:00.000 | 0.2 | 0.1 | 0.3 | 0.4 | 0.7 | 0.3 | 0.3 | 0.4 | 0.5 | 0.3 | 0.5 | 0.5 | 0.375 | 0.7 | 0.1 | 0.4 | 0.4 | 0.8 | 0.4 | 0.5 | 0.4 | 0.4 | 0.8 | 0.6 | 0.4 | 0.5 | 0.8 | 0.53333 | 0.8 | 0.4 | 0.7 | 0.7 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.4 | 0.53333 | 0.7 | 0.4
2026-05-15 | 20:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.4 | 0.1 | 0.1 | 0.1 | 0.6 | 0.1 | 0.3 | 0.1 | 0.1 | 0.6 | 0.1 | 0.1 | 0.2 | 0.5 | 0.24167 | 0.6 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0.14167 | 0.3 | 0.1
2026-05-15 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0
2026-05-15 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-15 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320