## PR_Calc
PR CALCULATION
16 MAGGIO 2026 | [67 empty] | 16 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 48
RAW PR | [64 empty] | 0.78506 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 78.5055
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 78.5394
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 78.4242
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-16 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7846.6
2026-05-16 | 00:15:00.000 | -0.6 | -0.00015 | 0 | 0 | -7.5e-05 | 0 | -7.5e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 00:45:00.000 | -0.8 | -0.0002 | 0 | 0 | -0.0001 | 0 | -0.0001 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 01:00:00.000 | -1 | -0.00025 | -0.6 | -0.00015 | -0.0002 | 0 | -0.0002 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 01:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 01:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 01:45:00.000 | -1 | -0.00025 | -0.6 | -0.00015 | -0.0002 | 0 | -0.0002 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 02:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 02:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 02:30:00.000 | -0.7 | -0.000175 | -0.5 | -0.000125 | -0.00015 | 0 | -0.00015 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 02:45:00.000 | -0.9 | -0.000225 | -0.3 | -7.5e-05 | -0.00015 | 0 | -0.00015 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 03:00:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 03:15:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 05:15:00.000 | -0.4 | -0.0001 | 0 | 0 | -5e-05 | 0 | -5e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 05:30:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 05:45:00.000 | -0.2 | -5e-05 | 0 | 0 | -2.5e-05 | 0 | -2.5e-05 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 06:15:00.000 | 2.1 | 0.000525 | 2.4 | 0.0006 | 0.0005625 | 0 | 0.0005625 | 0.13333 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 06:30:00.000 | 3.7 | 0.000925 | 4.3 | 0.001075 | 0.001 | 0 | 0.001 | 0.15 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 06:45:00.000 | 6.6 | 0.00165 | 6.5 | 0.001625 | 0.0016375 | 0 | 0.0016375 | 0.015267 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 07:00:00.000 | 7.3 | 0.001825 | 6.9 | 0.001725 | 0.001775 | 0 | 0.001775 | 0.056338 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 07:15:00.000 | 16 | 0.004 | 16 | 0.004 | 0.004 | 0 | 0.004 | 0 | 31187.2 | 31187.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 07:30:00.000 | 47 | 0.01175 | 47 | 0.01175 | 0.01175 | 0 | 0.01175 | 0 | 31187.2 | 31187.3 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 07:45:00.000 | 65.9 | 0.016475 | 65.1 | 0.016275 | 0.016375 | 65.5 | 0.016475 | 0.012214 | 31187.3 | 31187.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 08:00:00.000 | 89.4 | 0.02235 | 87.9 | 0.021975 | 0.022163 | 88.65 | 0.02235 | 0.01692 | 31187.4 | 31187.6 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 08:15:00.000 | 87.1 | 0.021775 | 84.4 | 0.0211 | 0.021437 | 85.75 | 0.021775 | 0.031487 | 31187.6 | 31187.9 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 08:30:00.000 | 136.6 | 0.03415 | 138.1 | 0.034525 | 0.034337 | 137.35 | 0.034525 | 0.010921 | 31187.9 | 31188.1 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 08:45:00.000 | 415.6 | 0.1039 | 445.7 | 0.11142 | 0.10766 | 430.65 | 0.11142 | 0.069894 | 31188.1 | 31189 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 09:00:00.000 | 353.9 | 0.088475 | 350.5 | 0.087625 | 0.08805 | 352.2 | 0.088475 | 0.0096536 | 31189 | 31189.9 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 09:15:00.000 | 431.3 | 0.10783 | 447.4 | 0.11185 | 0.10984 | 439.35 | 0.11185 | 0.036645 | 31189.9 | 31190.7 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 09:30:00.000 | 471.6 | 0.1179 | 409.3 | 0.10232 | 0.11011 | 440.45 | 0.1179 | 0.14145 | 31190.7 | 31192.3 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 09:45:00.000 | 652.9 | 0.16322 | 627.9 | 0.15698 | 0.1601 | 640.4 | 0.16322 | 0.039038 | 31192.3 | 31193.5 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 10:00:00.000 | 392.3 | 0.098075 | 312.6 | 0.07815 | 0.088113 | 352.45 | 0.098075 | 0.22613 | 31193.5 | 31194.8 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 10:15:00.000 | 998.8 | 0.2497 | 944.1 | 0.23603 | 0.24286 | 971.45 | 0.2497 | 0.056308 | 31194.8 | 31196.6 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 10:30:00.000 | 958.6 | 0.23965 | 935.2 | 0.2338 | 0.23673 | 946.9 | 0.23965 | 0.024712 | 31196.6 | 31198.8 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 10:45:00.000 | 807.7 | 0.20193 | 828 | 0.207 | 0.20446 | 817.85 | 0.207 | 0.024821 | 31198.8 | 31200.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 11:00:00.000 | 899.1 | 0.22478 | 927.6 | 0.2319 | 0.22834 | 913.35 | 0.2319 | 0.031204 | 31200.9 | 31202.9 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 11:15:00.000 | 746.8 | 0.1867 | 728.4 | 0.1821 | 0.1844 | 737.6 | 0.1867 | 0.024946 | 31202.9 | 31204.8 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 11:30:00.000 | 696.7 | 0.17418 | 677.2 | 0.1693 | 0.17174 | 686.95 | 0.17418 | 0.028386 | 31204.8 | 31206.7 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 11:45:00.000 | 713.5 | 0.17838 | 654.4 | 0.1636 | 0.17099 | 683.95 | 0.17838 | 0.08641 | 31206.7 | 31208.2 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 12:00:00.000 | 530.6 | 0.13265 | 457 | 0.11425 | 0.12345 | 493.8 | 0.13265 | 0.14905 | 31208.2 | 31209.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 12:15:00.000 | 700.2 | 0.17505 | 662.5 | 0.16562 | 0.17034 | 681.35 | 0.17505 | 0.055331 | 31209.7 | 31211.2 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 12:30:00.000 | 507.5 | 0.12687 | 501.5 | 0.12537 | 0.12612 | 504.5 | 0.12687 | 0.011893 | 31211.2 | 31212.7 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 12:45:00.000 | 822 | 0.2055 | 751.2 | 0.1878 | 0.19665 | 786.6 | 0.2055 | 0.090008 | 31212.7 | 31214.2 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 13:00:00.000 | 922.2 | 0.23055 | 924.4 | 0.2311 | 0.23083 | 923.3 | 0.2311 | 0.0023828 | 31214.2 | 31216.2 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 13:15:00.000 | 1027.3 | 0.25682 | 984.1 | 0.24602 | 0.25143 | 1005.7 | 0.25682 | 0.042955 | 31216.2 | 31218.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 13:30:00.000 | 1024.1 | 0.25603 | 982.5 | 0.24563 | 0.25083 | 1003.3 | 0.25603 | 0.041463 | 31218.6 | 31221 | 2400 | 0.8486 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 26.304 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 26.304 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 2.192 | 26.304 | 0.91501
2026-05-16 | 13:45:00.000 | 1034.4 | 0.2586 | 994.4 | 0.2486 | 0.2536 | 1014.4 | 0.2586 | 0.039432 | 31221 | 31223.5 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 14:00:00.000 | 1009.6 | 0.2524 | 975.5 | 0.24388 | 0.24814 | 992.55 | 0.2524 | 0.034356 | 31223.5 | 31225.9 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 14:15:00.000 | 1026 | 0.2565 | 988.1 | 0.24702 | 0.25176 | 1007.05 | 0.2565 | 0.037635 | 31225.9 | 31228.3 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 14:30:00.000 | 1019.6 | 0.2549 | 983.2 | 0.2458 | 0.25035 | 1001.4 | 0.2549 | 0.036349 | 31228.3 | 31230.7 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 14:45:00.000 | 1017.1 | 0.25428 | 984.4 | 0.2461 | 0.25019 | 1000.75 | 0.25428 | 0.032675 | 31230.7 | 31233.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 15:00:00.000 | 1026.1 | 0.25653 | 996.4 | 0.2491 | 0.25281 | 1011.25 | 0.25653 | 0.02937 | 31233.1 | 31235.6 | 2500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 15:15:00.000 | 912.7 | 0.22818 | 864.5 | 0.21613 | 0.22215 | 888.6 | 0.22818 | 0.054243 | 31235.6 | 31238 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 15:30:00.000 | 930.9 | 0.23272 | 905.7 | 0.22643 | 0.22958 | 918.3 | 0.23272 | 0.027442 | 31238 | 31240.1 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 15:45:00.000 | 1031.5 | 0.25788 | 1005.2 | 0.2513 | 0.25459 | 1018.35 | 0.25788 | 0.025826 | 31240.1 | 31242.5 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 16:00:00.000 | 1020.1 | 0.25503 | 980 | 0.245 | 0.25001 | 1000.05 | 0.25503 | 0.040098 | 31242.5 | 31244.9 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 16:15:00.000 | 945.6 | 0.2364 | 936.4 | 0.2341 | 0.23525 | 941 | 0.2364 | 0.0097768 | 31244.9 | 31247.2 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 16:30:00.000 | 818.2 | 0.20455 | 992.7 | 0.24818 | 0.22636 | 905.45 | 0.24818 | 0.19272 | 31247.2 | 31249.5 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 16:45:00.000 | 775.9 | 0.19397 | 869.3 | 0.21732 | 0.20565 | 822.6 | 0.21732 | 0.11354 | 31249.5 | 31251.6 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 17:00:00.000 | 512.1 | 0.12802 | 469 | 0.11725 | 0.12264 | 490.55 | 0.12802 | 0.087861 | 31251.6 | 31253.4 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 17:15:00.000 | 543.4 | 0.13585 | 519.4 | 0.12985 | 0.13285 | 531.4 | 0.13585 | 0.045164 | 31253.4 | 31254.7 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 17:30:00.000 | 521.9 | 0.13048 | 568.6 | 0.14215 | 0.13631 | 545.25 | 0.14215 | 0.085649 | 31254.7 | 31255.9 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 17:45:00.000 | 249.9 | 0.062475 | 245.9 | 0.061475 | 0.061975 | 247.9 | 0.062475 | 0.016136 | 31255.9 | 31256.9 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 18:00:00.000 | 305.1 | 0.076275 | 333.4 | 0.08335 | 0.079813 | 319.25 | 0.08335 | 0.088645 | 31256.9 | 31257.6 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 18:15:00.000 | 441.2 | 0.1103 | 521.5 | 0.13037 | 0.12034 | 481.35 | 0.13037 | 0.16682 | 31257.6 | 31258.6 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 18:30:00.000 | 379.7 | 0.094925 | 449.2 | 0.1123 | 0.10361 | 414.45 | 0.1123 | 0.16769 | 31258.6 | 31259.6 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 18:45:00.000 | 353.6 | 0.0884 | 429.8 | 0.10745 | 0.097925 | 391.7 | 0.10745 | 0.19454 | 31259.6 | 31260.6 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 19:00:00.000 | 256.9 | 0.064225 | 333.8 | 0.08345 | 0.073838 | 295.35 | 0.08345 | 0.26037 | 31260.6 | 31261.4 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 19:15:00.000 | 162 | 0.0405 | 227.2 | 0.0568 | 0.04865 | 194.6 | 0.0568 | 0.33505 | 31261.4 | 31261.9 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 19:30:00.000 | 89.9 | 0.022475 | 134.2 | 0.03355 | 0.028012 | 112.05 | 0.03355 | 0.39536 | 31261.9 | 31262.2 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 19:45:00.000 | 38 | 0.0095 | 60.6 | 0.01515 | 0.012325 | 0 | 0.012325 | 0.45842 | 31262.2 | 31262.3 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 20:00:00.000 | 27.9 | 0.006975 | 30 | 0.0075 | 0.0072375 | 0 | 0.0072375 | 0.072539 | 31262.3 | 31262.4 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 20:15:00.000 | 13.7 | 0.003425 | 14 | 0.0035 | 0.0034625 | 0 | 0.0034625 | 0.021661 | 31262.4 | 31262.5 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 20:30:00.000 | 1.3 | 0.000325 | 0.9 | 0.000225 | 0.000275 | 0 | 0.000275 | 0.36364 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 20:45:00.000 | -1.7 | -0.000425 | -2 | -0.0005 | -0.0004625 | 0 | -0.0004625 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 21:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 21:15:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 21:30:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 21:45:00.000 | -1.7 | -0.000425 | -2 | -0.0005 | -0.0004625 | 0 | -0.0004625 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 22:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 22:15:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 22:30:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 22:45:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 23:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 23:15:00.000 | -2 | -0.0005 | -1.5 | -0.000375 | -0.0004375 | 0 | -0.0004375 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 23:30:00.000 | -2.8 | -0.0007 | -2.5 | -0.000625 | -0.0006625 | 0 | -0.0006625 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
2026-05-16 | 23:45:00.000 | -2.8 | -0.0007 | -2 | -0.0005 | -0.0006 | 0 | -0.0006 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91501
PR for each inverter |  |  | 7.7401 |  | 7.6979 | 7.719 |  | 7.9575 |  |  |  | 75300 |  | 0.74352 | 0.75545 | 0.74728 | 0.77862 | 0.77644 | 0.76544 | 0.78947 | 0.79134 | 0.79598 | 0.77463 | 0.79687 | 0.83069 | #DIV/0! | #DIV/0! | #DIV/0! | 26.304 | 0.82461 | 0.78614 | 0.78671 | 0.81471 | 0.87612 | 0.79157 | 0.84022 | 0.8064 | 0.81078 | 0.83402 | 0.80258 | 0.80978 |  |  |  | 26.304 | 0.76668 | 0.7844 | 0.75717 | 0.76984 | 0.76722 | 0.74092 | 0.75129 | 0.74022 | 0.75151 | 0.77972 | 0.77756 | 0.75829 | #DIV/0! | #DIV/0! | #DIV/0! | 26.304 |  | 0.78539 |  | #DIV/0! | #DIV/0! | 7.9856e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-16 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 06:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 06:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 07:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 1.75 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 07:15:00.000 | 1.6 | 1.7 | 1.8 | 2 | 3.5 | 2.1 | 2.2 | 2.5 | 2.5 | 2.3 | 2.5 | 2.1 | 2.2333 | 3.5 | 1.6 | 2.1 | 2.2 | 4.2 | 2.1 | 3.5 | 2.3 | 2.6 | 4.9 | 2.5 | 2.3 | 2.6 | 4 | 2.9417 | 4.9 | 2.1 | 2.2 | 2.1 | 1.9 | 2 | 2 | 1.6 | 1.7 | 1.8 | 1.9 | 2.2 | 2.4 | 1.6 | 1.95 | 2.4 | 1.6
2026-05-16 | 07:30:00.000 | 5.9 | 12.9 | 5.7 | 13.2 | 12.8 | 13.1 | 12.2 | 15 | 14.5 | 14.6 | 14.5 | 14.4 | 12.4 | 15 | 5.7 | 12.7 | 13.2 | 13 | 12.5 | 13.3 | 14.6 | 14.6 | 15.2 | 14.9 | 13.4 | 14.6 | 15 | 13.9167 | 15.2 | 12.5 | 14.3 | 14 | 12.7 | 14.5 | 14.2 | 13.4 | 13.7 | 13.4 | 13.7 | 14.7 | 14.8 | 11.8 | 13.7667 | 14.8 | 11.8
2026-05-16 | 07:45:00.000 | 15.8 | 19.5 | 16.3 | 19.9 | 18.9 | 19.9 | 19.6 | 23.2 | 22.7 | 22 | 22.4 | 21.7 | 20.1583 | 23.2 | 15.8 | 19 | 18.9 | 19.4 | 18.7 | 20.2 | 22.4 | 22.1 | 22.9 | 22.9 | 21.8 | 21.9 | 22.8 | 21.0833 | 22.9 | 18.7 | 21.5 | 22 | 20.5 | 22 | 21.7 | 20.2 | 20.5 | 20.1 | 19.8 | 22.3 | 22.2 | 17.9 | 20.8917 | 22.3 | 17.9
2026-05-16 | 08:00:00.000 | 24.4 | 24.3 | 25 | 25.3 | 25 | 25.5 | 25.2 | 30.4 | 29.7 | 27.2 | 29.5 | 28.6 | 26.675 | 30.4 | 24.3 | 24.4 | 25.5 | 25.1 | 24.1 | 26.6 | 29.5 | 29.3 | 30.4 | 28.8 | 28.9 | 28.9 | 30.2 | 27.6417 | 30.4 | 24.1 | 29.6 | 28.6 | 26.3 | 28.7 | 27.3 | 24.8 | 26 | 25.6 | 25.7 | 29.2 | 28.7 | 22.7 | 26.9333 | 29.6 | 22.7
2026-05-16 | 08:15:00.000 | 24.2 | 24.2 | 24.6 | 25.2 | 25 | 24.9 | 25.1 | 30.5 | 29.7 | 28.2 | 29.4 | 28.6 | 26.6333 | 30.5 | 24.2 | 23.7 | 24.5 | 25.1 | 24 | 26.7 | 29.1 | 28.3 | 30.3 | 30.2 | 28.7 | 28.6 | 30 | 27.4333 | 30.3 | 23.7 | 29.3 | 28.5 | 25.1 | 28.3 | 27.6 | 23.9 | 25.5 | 23.4 | 25.2 | 28.9 | 28.4 | 22.8 | 26.4083 | 29.3 | 22.8
2026-05-16 | 08:30:00.000 | 36 | 36.1 | 36.3 | 37.4 | 37.4 | 36.4 | 37.1 | 45.6 | 44.5 | 42.4 | 44.4 | 43.2 | 39.7333 | 45.6 | 36 | 36.4 | 38.1 | 37 | 36.1 | 40.1 | 44.5 | 44.8 | 46.5 | 46.4 | 44.1 | 43.6 | 46.2 | 41.9833 | 46.5 | 36.1 | 45.2 | 43.9 | 39.6 | 41.5 | 43 | 38.3 | 38.9 | 37.2 | 38.1 | 44.2 | 43.5 | 34.2 | 40.6333 | 45.2 | 34.2
2026-05-16 | 08:45:00.000 | 112.6 | 116.3 | 98.9 | 112.5 | 98.3 | 96 | 113.3 | 133.8 | 128.9 | 120.9 | 130.8 | 133.3 | 116.3 | 133.8 | 96 | 97.1 | 97.6 | 112.8 | 86.5 | 109.7 | 139.9 | 124.8 | 138.3 | 132.7 | 122.5 | 124 | 120.7 | 117.2167 | 139.9 | 86.5 | 126 | 132.6 | 136.5 | 142.7 | 131.9 | 134.7 | 109.1 | 113 | 127.3 | 151 | 120.9 | 114.4 | 128.3417 | 151 | 109.1
2026-05-16 | 09:00:00.000 | 95.8 | 93.2 | 93.2 | 101.6 | 99.1 | 93.1 | 99.4 | 110.3 | 107.6 | 99.2 | 107.9 | 103.5 | 100.325 | 110.3 | 93.1 | 90.7 | 102.2 | 89.2 | 106.2 | 103.2 | 106.5 | 110.3 | 108.5 | 108.7 | 101.9 | 106.2 | 113.4 | 103.9167 | 113.4 | 89.2 | 110.7 | 102.8 | 104.4 | 107.8 | 118.1 | 95.1 | 105.7 | 108.2 | 104.6 | 108.7 | 106.2 | 101.2 | 106.125 | 118.1 | 95.1
2026-05-16 | 09:15:00.000 | 112.7 | 112.6 | 118.6 | 113.8 | 113.3 | 119 | 116.3 | 119.1 | 127.4 | 130.1 | 128.9 | 125.4 | 119.7667 | 130.1 | 112.6 | 116.4 | 124.2 | 118.1 | 119.1 | 123.8 | 124.1 | 130.9 | 131.9 | 135.2 | 121.9 | 129.7 | 123.8 | 124.925 | 135.2 | 116.4 | 123.3 | 128.1 | 122.6 | 128.2 | 128.2 | 120.5 | 110.2 | 115.6 | 116.7 | 125.5 | 123.6 | 109.8 | 121.025 | 128.2 | 109.8
2026-05-16 | 09:30:00.000 | 134.6 | 139.3 | 137.4 | 146.3 | 141 | 136.7 | 140.8 | 144.2 | 148.9 | 142.8 | 135.7 | 138.4 | 140.5083 | 148.9 | 134.6 | 136.7 | 145 | 141.8 | 138.9 | 140.1 | 140.8 | 143.2 | 139.7 | 137.8 | 144.9 | 143.1 | 146.1 | 141.5083 | 146.1 | 136.7 | 123.3 | 131.4 | 116 | 121.5 | 127 | 113.5 | 127.4 | 128.4 | 127.2 | 133.6 | 131.2 | 115.1 | 124.6333 | 133.6 | 113.5
2026-05-16 | 09:45:00.000 | 172.5 | 178.8 | 151.1 | 190.2 | 181.6 | 172.2 | 194.5 | 183.4 | 191.6 | 174.6 | 184.7 | 192.4 | 180.6333 | 194.5 | 151.1 | 195.9 | 192.3 | 190.4 | 174.9 | 184.2 | 195.7 | 192.2 | 187.3 | 189 | 189.6 | 187.7 | 200.5 | 189.975 | 200.5 | 174.9 | 200.7 | 170.5 | 164.6 | 173.1 | 166 | 165.5 | 184.1 | 185.3 | 172.2 | 175.8 | 176.5 | 144.7 | 173.25 | 200.7 | 144.7
2026-05-16 | 10:00:00.000 | 104.8 | 106 | 107.3 | 126.1 | 118.8 | 111.7 | 141 | 114.9 | 126.8 | 111.9 | 125.6 | 132.4 | 118.9417 | 141 | 104.8 | 135.9 | 145.2 | 129.3 | 143.5 | 138.8 | 128.3 | 121.9 | 124.6 | 114.1 | 129.5 | 143 | 137.5 | 132.6333 | 145.2 | 114.1 | 97.6 | 97.9 | 78.6 | 86.4 | 89.1 | 80.4 | 89.4 | 71.4 | 79.3 | 84.6 | 102.7 | 78.5 | 86.325 | 102.7 | 71.4
2026-05-16 | 10:15:00.000 | 242.8 | 258.2 | 272.3 | 268.2 | 279.5 | 269.7 | 277 | 262.4 | 270.4 | 274.4 | 272.6 | 281.2 | 269.0583 | 281.2 | 242.8 | 273.1 | 280.1 | 272.6 | 271.1 | 281.3 | 278.8 | 279.2 | 263.1 | 277.9 | 272.5 | 268.6 | 260.8 | 273.2583 | 281.3 | 260.8 | 269.3 | 266.3 | 265.2 | 246.6 | 251 | 235.3 | 256.4 | 252.3 | 261.9 | 259.7 | 255.5 | 237.3 | 254.7333 | 269.3 | 235.3
2026-05-16 | 10:30:00.000 | 233 | 238.2 | 251.2 | 248.8 | 245.6 | 247.7 | 254.8 | 259.1 | 253.3 | 251.3 | 265 | 253.8 | 250.15 | 265 | 233 | 239.6 | 232.2 | 239.5 | 241.8 | 239.4 | 251.7 | 256.8 | 258.4 | 261.2 | 244.5 | 248.9 | 246.8 | 246.7333 | 261.2 | 232.2 | 256.7 | 257.6 | 252.4 | 246.3 | 207.5 | 219.3 | 230.4 | 240.7 | 237.2 | 248 | 250.1 | 209 | 237.9333 | 257.6 | 207.5
2026-05-16 | 10:45:00.000 | 212 | 202.5 | 203.7 | 193.5 | 202.7 | 206.7 | 189.2 | 207 | 203.1 | 216.8 | 205.3 | 209.6 | 204.3417 | 216.8 | 189.2 | 217.4 | 232.7 | 210.6 | 224.8 | 226.9 | 204.5 | 221.4 | 213 | 215 | 204.9 | 229.9 | 238 | 219.925 | 238 | 204.5 | 205.4 | 230.6 | 216.1 | 208.1 | 223.2 | 211.3 | 204.8 | 194.1 | 205.6 | 207.2 | 219.2 | 202.5 | 210.675 | 230.6 | 194.1
2026-05-16 | 11:00:00.000 | 238.3 | 230.9 | 228.2 | 239.9 | 230.8 | 248.3 | 235.6 | 240.3 | 244.1 | 230.3 | 249.5 | 246.2 | 238.5333 | 249.5 | 228.2 | 254.8 | 248.9 | 246.6 | 237.7 | 257.5 | 232.4 | 240.3 | 244 | 251.7 | 240 | 252.6 | 245.5 | 246 | 257.5 | 232.4 | 231.6 | 235 | 240.9 | 246.1 | 241 | 244.2 | 251.1 | 247.4 | 251 | 247.6 | 236.4 | 237.9 | 242.5167 | 251.1 | 231.6
2026-05-16 | 11:15:00.000 | 180.8 | 168.3 | 172.3 | 181.9 | 189.9 | 198.3 | 206.4 | 180.5 | 193.7 | 183.8 | 194.2 | 206 | 188.0083 | 206.4 | 168.3 | 217.7 | 219 | 223.2 | 207.3 | 221.4 | 190.4 | 207.1 | 204.4 | 211.5 | 208 | 226.8 | 224.9 | 213.475 | 226.8 | 190.4 | 205.4 | 190.6 | 183.2 | 185.5 | 178 | 174.5 | 165.3 | 186.4 | 182.1 | 188.9 | 196 | 176.9 | 184.4 | 205.4 | 165.3
2026-05-16 | 11:30:00.000 | 178.7 | 170.3 | 172.2 | 172.7 | 180.2 | 167.5 | 188.2 | 188.5 | 181.2 | 186.6 | 181.9 | 191 | 179.9167 | 191 | 167.5 | 185.3 | 183.9 | 186.6 | 188.5 | 196.8 | 165.6 | 189.5 | 196.1 | 196.9 | 192.6 | 192.3 | 193.9 | 189 | 196.9 | 165.6 | 169.9 | 185.6 | 174.3 | 176.3 | 187.6 | 164.7 | 183.1 | 175.4 | 168.2 | 179.1 | 185.3 | 172.5 | 176.8333 | 187.6 | 164.7
2026-05-16 | 11:45:00.000 | 184.6 | 189.4 | 170.5 | 210.3 | 182.4 | 188.6 | 222.5 | 197.6 | 212.4 | 185.6 | 207.4 | 206.7 | 196.5 | 222.5 | 170.5 | 200.2 | 207.8 | 206 | 199.6 | 218.4 | 209.5 | 189.1 | 203.5 | 199.4 | 194.1 | 209.4 | 205 | 203.5 | 218.4 | 189.1 | 167.8 | 179.3 | 171.3 | 186.3 | 182.5 | 180.6 | 177.1 | 162.2 | 179.3 | 185.1 | 187.5 | 165.8 | 177.0667 | 187.5 | 162.2
2026-05-16 | 12:00:00.000 | 123 | 127.7 | 127.7 | 128 | 151.1 | 140.5 | 149.1 | 149.8 | 147.2 | 141 | 147.2 | 152.7 | 140.4167 | 152.7 | 123 | 153 | 155.6 | 163.7 | 162.3 | 176.5 | 151.1 | 150.2 | 161.4 | 170.6 | 159.7 | 159.9 | 155.5 | 159.9583 | 176.5 | 150.2 | 133.5 | 135.7 | 126.1 | 131.9 | 114.9 | 99.2 | 110.5 | 113.8 | 120.1 | 135.7 | 135.5 | 97.4 | 121.1917 | 135.7 | 97.4
2026-05-16 | 12:15:00.000 | 190.2 | 202 | 168.8 | 215.7 | 188.8 | 184.2 | 198.8 | 209.8 | 206 | 202.4 | 210.1 | 204.3 | 198.425 | 215.7 | 168.8 | 178.6 | 190.3 | 188.4 | 189 | 188.8 | 206.5 | 202.9 | 210.3 | 203.5 | 211.7 | 186.4 | 203.2 | 196.6333 | 211.7 | 178.6 | 158.6 | 176.4 | 169.9 | 181.3 | 182.7 | 177.6 | 169.4 | 165.6 | 165.2 | 173.1 | 165.2 | 158.9 | 170.325 | 182.7 | 158.6
2026-05-16 | 12:30:00.000 | 121.5 | 124 | 132 | 128.4 | 140.4 | 142.7 | 135 | 138.7 | 145.6 | 148.9 | 154.5 | 150.7 | 138.5333 | 154.5 | 121.5 | 155.5 | 157.5 | 147 | 158.4 | 173.5 | 151 | 156.8 | 153.6 | 155.7 | 162.3 | 171.9 | 166.2 | 159.1167 | 173.5 | 147 | 131 | 145 | 129.2 | 136.4 | 144.8 | 129 | 129.2 | 132 | 135.9 | 140.7 | 131.9 | 104.3 | 132.45 | 145 | 104.3
2026-05-16 | 12:45:00.000 | 212.1 | 202.7 | 191.1 | 203.2 | 210.1 | 209.6 | 222.2 | 212.8 | 216.5 | 199.2 | 211.6 | 221.8 | 209.4083 | 222.2 | 191.1 | 216.3 | 216.9 | 225.3 | 222.8 | 214.8 | 213.8 | 212.3 | 212.4 | 220.1 | 209.5 | 213.2 | 216 | 216.1167 | 225.3 | 209.5 | 158.6 | 203.2 | 180.1 | 192.1 | 189.6 | 173.8 | 187 | 172.7 | 195.4 | 200.3 | 201.4 | 185.4 | 186.6333 | 203.2 | 158.6
2026-05-16 | 13:00:00.000 | 223.1 | 227.6 | 243.1 | 242.8 | 255.4 | 242.6 | 257.3 | 243.2 | 251.9 | 249.8 | 250.5 | 259.1 | 245.5333 | 259.1 | 223.1 | 247.7 | 247.2 | 256.2 | 249.6 | 259.8 | 251.8 | 253.6 | 260.8 | 257.2 | 255.9 | 255.2 | 254.8 | 254.15 | 260.8 | 247.2 | 207.7 | 244.7 | 253.3 | 268 | 263.1 | 263 | 260.8 | 252.1 | 246.1 | 260.3 | 244.8 | 238.7 | 250.2167 | 268 | 207.7
2026-05-16 | 13:15:00.000 | 266.2 | 269.9 | 270 | 274.4 | 274.6 | 268.2 | 271.6 | 281.6 | 281.3 | 281.5 | 281.9 | 281 | 275.1833 | 281.9 | 266.2 | 267.1 | 268.7 | 266.6 | 262.6 | 281 | 281.1 | 281.6 | 281.2 | 281.2 | 281.5 | 281.2 | 281.6 | 276.2833 | 281.6 | 262.6 | 229.4 | 281.7 | 277.3 | 281.2 | 281.5 | 281.1 | 281.4 | 278.9 | 276.5 | 271.8 | 281.6 | 260.5 | 273.575 | 281.7 | 229.4
2026-05-16 | 13:30:00.000 | 264.6 | 268.2 | 268.2 | 262.9 | 272.8 | 266.9 | 270.6 | 281.3 | 281.1 | 281.3 | 281.7 | 281.1 | 273.3917 | 281.7 | 262.9 | 265.9 | 266.4 | 264.6 | 261.4 | 280.7 | 280.9 | 281.4 | 280.9 | 280.9 | 281.6 | 281 | 281.3 | 275.5833 | 281.6 | 261.4 | 231.8 | 280.7 | 281 | 280.9 | 281.3 | 280.4 | 280.8 | 277.8 | 280.7 | 280.9 | 281 | 258.1 | 274.6167 | 281.3 | 231.8
2026-05-16 | 13:45:00.000 | 266 | 269.7 | 269.8 | 274.2 | 274.6 | 268.8 | 272.8 | 281.6 | 281.4 | 281.6 | 282 | 281.1 | 275.3 | 282 | 266 | 267.9 | 267.5 | 265.8 | 262.8 | 281.1 | 281.2 | 281.7 | 281.3 | 281.3 | 281.6 | 281.3 | 281.6 | 276.2583 | 281.7 | 262.8 | 271.4 | 281 | 281.3 | 281.3 | 281.7 | 280.9 | 281 | 279.4 | 281.1 | 281.1 | 281.3 | 260.1 | 278.4667 | 281.7 | 260.1
2026-05-16 | 14:00:00.000 | 255 | 257 | 263.5 | 255.9 | 266.7 | 246.9 | 255.8 | 267.6 | 266.7 | 278.3 | 267.7 | 272.6 | 262.8083 | 278.3 | 246.9 | 252.3 | 248.5 | 249.1 | 244.1 | 260 | 267.2 | 280.6 | 267.9 | 272.3 | 274.5 | 272 | 256.8 | 262.1083 | 280.6 | 244.1 | 277.8 | 276.4 | 274 | 275.7 | 278.7 | 277.9 | 274.6 | 271.5 | 273.2 | 273.7 | 274.8 | 247.6 | 272.9917 | 278.7 | 247.6
2026-05-16 | 14:15:00.000 | 263.3 | 267 | 266.7 | 271.9 | 271.2 | 266.2 | 270 | 281.5 | 281.3 | 281.4 | 281.4 | 281.4 | 273.6083 | 281.5 | 263.3 | 265.4 | 262.3 | 262 | 259.6 | 281 | 281.2 | 281.4 | 281.4 | 281.4 | 281 | 281.1 | 281.5 | 274.9417 | 281.5 | 259.6 | 281.1 | 281.8 | 281.7 | 281.7 | 281.4 | 279.4 | 279.6 | 276.4 | 280.6 | 281.6 | 281.3 | 257.3 | 278.6583 | 281.8 | 257.3
2026-05-16 | 14:30:00.000 | 261.1 | 264.8 | 264.7 | 270.1 | 269.5 | 264 | 267.2 | 281.5 | 281.3 | 281.1 | 281.4 | 281.4 | 272.3417 | 281.5 | 261.1 | 257 | 253.6 | 253.1 | 250.9 | 278.5 | 281.2 | 281.3 | 281.4 | 281.4 | 281 | 281.1 | 281.5 | 271.8333 | 281.5 | 250.9 | 281.1 | 281.8 | 281.8 | 281.6 | 281.2 | 279.4 | 280.8 | 275.4 | 280 | 281.4 | 272.2 | 255.5 | 277.6833 | 281.8 | 255.5
2026-05-16 | 14:45:00.000 | 259.7 | 263.3 | 263.7 | 268.8 | 268.3 | 263.1 | 266.5 | 281.5 | 281.3 | 281.1 | 281.4 | 281.4 | 271.675 | 281.5 | 259.7 | 262.9 | 257 | 257.7 | 256.5 | 281.6 | 281.2 | 281.2 | 281.4 | 281.4 | 281 | 281.1 | 281.5 | 273.7083 | 281.6 | 256.5 | 281.1 | 281.8 | 281.1 | 281.6 | 281.2 | 278.9 | 280.9 | 274.7 | 279.5 | 281.4 | 281.3 | 254.8 | 278.1917 | 281.8 | 254.8
2026-05-16 | 15:00:00.000 | 261.7 | 265.3 | 265.6 | 270.7 | 270.4 | 265.2 | 268.8 | 281.5 | 281.2 | 281 | 281.3 | 281.4 | 272.8417 | 281.5 | 261.7 | 265 | 257.7 | 259.1 | 258.3 | 281.6 | 281.1 | 281.2 | 281.4 | 281.4 | 281 | 281.1 | 281.5 | 274.2 | 281.6 | 257.7 | 281.1 | 281.7 | 281.1 | 281.5 | 281.2 | 280.6 | 280.8 | 276.9 | 281.1 | 281.3 | 281.3 | 256.6 | 278.7667 | 281.7 | 256.6
2026-05-16 | 15:15:00.000 | 237.3 | 239 | 241.7 | 255.2 | 267.8 | 265.7 | 274.8 | 252.6 | 259.4 | 257.5 | 268.7 | 264.4 | 257.0083 | 274.8 | 237.3 | 268.2 | 263.7 | 263.7 | 264.4 | 279.8 | 274.8 | 279 | 274.7 | 279 | 281.3 | 280.3 | 271.7 | 273.3833 | 281.3 | 263.7 | 253 | 246.6 | 236.5 | 241.1 | 234.9 | 234.2 | 237.1 | 245.9 | 238.9 | 235.9 | 246.6 | 223.5 | 239.5167 | 253 | 223.5
2026-05-16 | 15:30:00.000 | 224.6 | 235.1 | 237.1 | 253.8 | 243.3 | 238.1 | 242.2 | 258.7 | 261.7 | 238.4 | 260.3 | 261.3 | 246.2167 | 261.7 | 224.6 | 255.9 | 247.1 | 251.6 | 247.2 | 267.7 | 250.7 | 262.3 | 261 | 267.4 | 263.5 | 254.9 | 265.4 | 257.8917 | 267.7 | 247.1 | 259.1 | 244.3 | 251.4 | 233.2 | 231.1 | 236.4 | 237.8 | 253.2 | 249.3 | 230.1 | 267.3 | 211.2 | 242.0333 | 267.3 | 211.2
2026-05-16 | 15:45:00.000 | 261.8 | 265.9 | 266.7 | 271.5 | 271.5 | 266.3 | 270.2 | 281.8 | 281.3 | 281.1 | 281.2 | 281.1 | 273.3667 | 281.8 | 261.8 | 264.8 | 254.6 | 258.6 | 258.8 | 279.7 | 281.1 | 281.6 | 281.2 | 281.4 | 281.4 | 279 | 278.2 | 273.3667 | 281.6 | 254.6 | 281.1 | 281.5 | 271.5 | 260.9 | 281.3 | 280.2 | 279.4 | 274.5 | 278.8 | 281.4 | 271.8 | 256.6 | 274.9167 | 281.5 | 256.6
2026-05-16 | 16:00:00.000 | 248.3 | 258.7 | 254.4 | 265.8 | 269.3 | 253.3 | 267.6 | 274.5 | 273.6 | 272.2 | 275.6 | 276.5 | 265.8167 | 276.5 | 248.3 | 261.5 | 252.1 | 252.9 | 244.8 | 267.5 | 278.5 | 278.1 | 280.1 | 278.3 | 265.5 | 278 | 278.9 | 268.0167 | 280.1 | 244.8 | 275.8 | 272 | 266.5 | 256.1 | 263.8 | 250.9 | 257.3 | 262.3 | 261.6 | 261.4 | 275.3 | 241.9 | 262.075 | 275.8 | 241.9
2026-05-16 | 16:15:00.000 | 237.6 | 242 | 239.9 | 243.8 | 233.9 | 236 | 225.1 | 257.2 | 250.3 | 246.1 | 249.6 | 254.2 | 242.975 | 257.2 | 225.1 | 235.9 | 227.4 | 229.1 | 222.9 | 247.7 | 249.5 | 265.4 | 254.7 | 254.9 | 250.6 | 250.7 | 259.2 | 245.6667 | 265.4 | 222.9 | 267.8 | 259.7 | 251.7 | 260.6 | 255.9 | 253.5 | 261 | 248.2 | 250.1 | 259.9 | 261.2 | 232.4 | 255.1667 | 267.8 | 232.4
2026-05-16 | 16:30:00.000 | 212.8 | 209 | 215.2 | 219.8 | 217.9 | 215.4 | 221.4 | 259.3 | 255.2 | 245.4 | 251.7 | 245.3 | 230.7 | 259.3 | 209 | 250.3 | 250.9 | 252.9 | 253.2 | 280.5 | 277.9 | 281.9 | 281.2 | 281.2 | 281.1 | 281.3 | 281.1 | 271.125 | 281.9 | 250.3 | 277.7 | 281.1 | 281 | 281.3 | 281.5 | 278.2 | 280.6 | 271.3 | 278.9 | 271.6 | 280.5 | 252.1 | 276.3167 | 281.5 | 252.1
2026-05-16 | 16:45:00.000 | 201.6 | 210.9 | 194.5 | 207.4 | 209 | 211.3 | 210.4 | 228.9 | 232.3 | 213.6 | 216 | 234.1 | 214.1667 | 234.1 | 194.5 | 230.4 | 233.6 | 228.5 | 239.8 | 247.9 | 237.6 | 245.8 | 262 | 263.3 | 255.5 | 251.2 | 248 | 245.3 | 263.3 | 228.5 | 232.5 | 248.1 | 229.5 | 232.8 | 242.8 | 221.4 | 240 | 212.6 | 217.4 | 231.8 | 227.9 | 193.6 | 227.5333 | 248.1 | 193.6
2026-05-16 | 17:00:00.000 | 123.4 | 132.4 | 139.9 | 148.4 | 153.2 | 155.6 | 174.5 | 153.9 | 156.1 | 164.4 | 180.4 | 171.8 | 154.5 | 180.4 | 123.4 | 175.5 | 166.3 | 173 | 175.4 | 191.4 | 176.4 | 184.1 | 184.6 | 182.3 | 184.8 | 187.9 | 189.1 | 180.9 | 191.4 | 166.3 | 128.6 | 126.7 | 130.7 | 131.6 | 133.9 | 129 | 112.1 | 124.6 | 127.1 | 133 | 135.1 | 121 | 127.7833 | 135.1 | 112.1
2026-05-16 | 17:15:00.000 | 129.3 | 136.9 | 132.3 | 140.3 | 129.5 | 141.8 | 140.1 | 153.1 | 156.4 | 148.1 | 168.1 | 150.5 | 143.8667 | 168.1 | 129.3 | 133.3 | 122.2 | 135.8 | 124 | 145.5 | 165.7 | 161.6 | 150 | 153.7 | 149.8 | 152.2 | 153.7 | 145.625 | 165.7 | 122.2 | 152 | 153.4 | 141 | 144.2 | 151.5 | 151.2 | 158.4 | 139.3 | 132.6 | 152.7 | 143.9 | 154.4 | 147.8833 | 158.4 | 132.6
2026-05-16 | 17:30:00.000 | 123.3 | 127 | 115.7 | 125.4 | 109.2 | 116.5 | 121.2 | 147.6 | 154 | 144.1 | 138 | 140.9 | 130.2417 | 154 | 109.2 | 119.7 | 119.8 | 119.5 | 111.3 | 141.2 | 147.6 | 152.3 | 153 | 154.5 | 149.5 | 139.8 | 151.6 | 138.3167 | 154.5 | 111.3 | 164.1 | 145.6 | 153.6 | 165 | 175.6 | 150.4 | 152.8 | 139.9 | 144.5 | 149.5 | 154.2 | 138.1 | 152.775 | 175.6 | 138.1
2026-05-16 | 17:45:00.000 | 63.2 | 65.5 | 66.9 | 72 | 72.7 | 80.8 | 90.8 | 80.5 | 85.8 | 84.9 | 93.3 | 85.7 | 78.5083 | 93.3 | 63.2 | 87.3 | 88.9 | 92.5 | 97.7 | 108.9 | 84.2 | 96.2 | 90.8 | 95.8 | 98.5 | 107.5 | 113 | 96.775 | 113 | 84.2 | 85 | 72.4 | 72.1 | 69.1 | 65 | 57 | 62.6 | 63.9 | 70 | 78 | 74 | 65.6 | 69.5583 | 85 | 57
2026-05-16 | 18:00:00.000 | 68.4 | 77.3 | 71.5 | 80.9 | 79 | 70.8 | 81.5 | 101.5 | 104.3 | 83.7 | 97.3 | 92.8 | 84.0833 | 104.3 | 68.4 | 79.7 | 80.1 | 77.9 | 80.3 | 94.1 | 95.4 | 99.1 | 95.1 | 102.1 | 98.2 | 98.6 | 106.4 | 92.25 | 106.4 | 77.9 | 102.3 | 100.1 | 83.1 | 86.7 | 83.6 | 83 | 65.4 | 77.5 | 87.3 | 97.3 | 98 | 63.6 | 85.6583 | 102.3 | 63.6
2026-05-16 | 18:15:00.000 | 115.3 | 114.2 | 110.6 | 111.9 | 111.4 | 111.2 | 101.7 | 142.3 | 142 | 131.7 | 136.4 | 128.7 | 121.45 | 142.3 | 101.7 | 103 | 106.2 | 102.3 | 101.5 | 120.2 | 127.1 | 127.8 | 133.2 | 131.8 | 126.7 | 121.3 | 131.8 | 119.4083 | 133.2 | 101.5 | 150.2 | 164.1 | 135.8 | 155.3 | 135.2 | 125 | 136.4 | 122.9 | 126.8 | 152.6 | 146.8 | 115.3 | 138.8667 | 164.1 | 115.3
2026-05-16 | 18:30:00.000 | 93.6 | 92.6 | 87.5 | 87.6 | 88 | 84.4 | 82 | 123.8 | 116.9 | 108.1 | 114.3 | 105.7 | 98.7083 | 123.8 | 82 | 84.3 | 84.9 | 83.6 | 80 | 94.8 | 101.1 | 101.6 | 107.8 | 110.4 | 102.4 | 94.5 | 105.5 | 95.9083 | 110.4 | 80 | 133.7 | 124.2 | 114.7 | 121.6 | 123.6 | 115.7 | 115 | 111.7 | 115.7 | 136.4 | 131.1 | 108.4 | 120.9833 | 136.4 | 108.4
2026-05-16 | 18:45:00.000 | 84 | 89 | 88.2 | 90 | 89 | 84.8 | 83 | 123.6 | 114.2 | 107 | 117.8 | 105.8 | 98.0333 | 123.6 | 83 | 84.2 | 80.4 | 84.3 | 80.1 | 94.5 | 98.9 | 104.2 | 108.7 | 108.3 | 101 | 96 | 103.2 | 95.3167 | 108.7 | 80.1 | 126.9 | 124.3 | 106.3 | 115.5 | 111.1 | 99.8 | 100.4 | 100.6 | 102.2 | 129.7 | 120 | 92.7 | 110.7917 | 129.7 | 92.7
2026-05-16 | 19:00:00.000 | 63.6 | 64.8 | 63.8 | 65.6 | 66.2 | 62.5 | 60.6 | 92.1 | 88.6 | 82.2 | 87.9 | 79.4 | 73.1083 | 92.1 | 60.6 | 62.6 | 59.1 | 63.8 | 59.5 | 69.9 | 75.7 | 77.3 | 79.5 | 78.7 | 73.3 | 68.9 | 74.8 | 70.2583 | 79.5 | 59.1 | 94.5 | 92.4 | 78 | 82.2 | 81.3 | 73.4 | 76.9 | 74.3 | 75.4 | 93.7 | 88.7 | 68.6 | 81.6167 | 94.5 | 68.6
2026-05-16 | 19:15:00.000 | 40 | 40.7 | 39.6 | 41 | 41.4 | 38.3 | 38 | 60.2 | 57.5 | 52.5 | 56.2 | 50.4 | 46.3167 | 60.2 | 38 | 38.5 | 37.3 | 39.7 | 35.5 | 42.2 | 46 | 47.1 | 48.2 | 47.5 | 42.8 | 39.2 | 45 | 42.4167 | 48.2 | 35.5 | 61.5 | 59.9 | 50.1 | 54.8 | 49.8 | 46.8 | 49.9 | 47.9 | 51.3 | 64.4 | 57.2 | 42.6 | 53.0167 | 64.4 | 42.6
2026-05-16 | 19:30:00.000 | 21 | 21.2 | 20.6 | 21.6 | 21.9 | 20.1 | 21.2 | 32.9 | 31.5 | 28.7 | 30.5 | 27 | 24.85 | 32.9 | 20.1 | 19.8 | 19.7 | 21.2 | 17.4 | 20.4 | 23.1 | 23.6 | 24.7 | 24.1 | 22.4 | 20.5 | 22.5 | 21.6167 | 24.7 | 17.4 | 33.3 | 33 | 27.8 | 30.4 | 28.9 | 25.2 | 27.1 | 25.9 | 28.4 | 36.3 | 30.4 | 24.8 | 29.2917 | 36.3 | 24.8
2026-05-16 | 19:45:00.000 | 8.3 | 8.3 | 8.1 | 8.6 | 8.7 | 8.2 | 9.1 | 13.1 | 12.6 | 11.5 | 11.9 | 11 | 9.95 | 13.1 | 8.1 | 8.1 | 9.1 | 8.9 | 7.4 | 9.4 | 10.2 | 11 | 11.8 | 12.1 | 12.3 | 11.6 | 13.4 | 10.4417 | 13.4 | 7.4 | 13.2 | 13.7 | 11.5 | 12.5 | 12.1 | 10.1 | 11 | 10.6 | 11.6 | 14.5 | 12.1 | 10.1 | 11.9167 | 14.5 | 10.1
2026-05-16 | 20:00:00.000 | 6.4 | 6.4 | 6.3 | 6.4 | 6.6 | 6.3 | 6 | 8.1 | 7.9 | 7.3 | 7.5 | 7.2 | 6.8667 | 8.1 | 6 | 6.3 | 6.3 | 6.4 | 6.2 | 7.5 | 7.8 | 8.2 | 8.5 | 8.8 | 8.5 | 8.3 | 8.8 | 7.6333 | 8.8 | 6.2 | 7.6 | 7.6 | 6.6 | 7.2 | 7.1 | 5.9 | 6.3 | 6.2 | 6.6 | 8.1 | 7.2 | 6 | 6.8667 | 8.1 | 5.9
2026-05-16 | 20:15:00.000 | 3.6 | 3.5 | 3.6 | 3.7 | 3.7 | 3.8 | 3.7 | 4.5 | 4.6 | 4.4 | 4.5 | 4.3 | 3.9917 | 4.6 | 3.5 | 3.6 | 3.6 | 3.6 | 3.5 | 4 | 4.2 | 4.5 | 4.7 | 4.7 | 4.4 | 4.4 | 4.8 | 4.1667 | 4.8 | 3.5 | 4.6 | 4.2 | 3.9 | 4.2 | 4.3 | 3.7 | 3.8 | 3.8 | 3.9 | 4.5 | 4.4 | 3.4 | 4.0583 | 4.6 | 3.4
2026-05-16 | 20:30:00.000 | 0.5 | 0.3 | 0.6 | 0.8 | 0.8 | 0.6 | 0.7 | 0.8 | 0.9 | 0.7 | 0.8 | 0.8 | 0.69167 | 0.9 | 0.3 | 0.6 | 0.7 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.8 | 0.8 | 0.9 | 0.775 | 0.9 | 0.6 | 0.8 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.825 | 0.9 | 0.7
2026-05-16 | 20:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13333 | 0.5 | 0.1 | 0.1 | 0.1 | 0.9 | 0.1 | 0.3 | 0.1 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.3 | 0.225 | 0.9 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0.125 | 0.3 | 0.1
2026-05-16 | 21:00:00.000 | 0 | 0 | 0 | 0.1 | 0.2 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.11667 | 0.2 | 0 | 0 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0.13 | 0.4 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0
2026-05-16 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-16 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320