## PR_Calc
PR CALCULATION
17 MAGGIO 2026 | [67 empty] | 17 May 2026 PR Calculation
Total VALUES | [64 empty] | 96 |  |  | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [64 empty] | 0.897 |  |  | Total values with POA>50 | 52
RAW PR | [64 empty] | 0.78928 |  |  | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [64 empty] | 0.03 |  |  | RAW PR (calculated with each power and POA value) [%] | 78.9275
Irradiance Minimum Value Accepted for calculation [%] | [64 empty] | 50 |  |  | Average of each PR [%] | 78.9382
NOMINAL VALUES | [67 empty] | PR from SCADA [%] | 48.0685
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  |  |  |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  |  |  |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 | [10 empty] | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  |  |  |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  |  |  |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 | [10 empty] | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  |  |  |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Energy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | TX1 Total loss | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power | Enegy Loss for TX3 kW/H | Normal PR calculation | Compensated PR | inverter sum test | Internal Availability [%] | External Availability [%] | PR after adjustments
2026-05-17 | 00:00:00.000 | -2.6 | -0.00065 | -2.6 | -0.00065 | -0.00065 | 0 | -0.00065 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4688.7
2026-05-17 | 00:15:00.000 | -2.1 | -0.000525 | -1.7 | -0.000425 | -0.000475 | 0 | -0.000475 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 00:30:00.000 | -2 | -0.0005 | -1 | -0.00025 | -0.000375 | 0 | -0.000375 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 00:45:00.000 | -1.5 | -0.000375 | -0.5 | -0.000125 | -0.00025 | 0 | -0.00025 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 01:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 01:15:00.000 | -1.6 | -0.0004 | -1.1 | -0.000275 | -0.0003375 | 0 | -0.0003375 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 01:30:00.000 | -1.5 | -0.000375 | -1.4 | -0.00035 | -0.0003625 | 0 | -0.0003625 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 01:45:00.000 | -2 | -0.0005 | -1.9 | -0.000475 | -0.0004875 | 0 | -0.0004875 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 02:00:00.000 | -1.4 | -0.00035 | -1.1 | -0.000275 | -0.0003125 | 0 | -0.0003125 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 02:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 02:30:00.000 | -1.3 | -0.000325 | -1 | -0.00025 | -0.0002875 | 0 | -0.0002875 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 02:45:00.000 | -1.8 | -0.00045 | -1.9 | -0.000475 | -0.0004625 | 0 | -0.0004625 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 03:00:00.000 | -1.7 | -0.000425 | -1.7 | -0.000425 | -0.000425 | 0 | -0.000425 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 03:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 03:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 03:45:00.000 | -0.3 | -7.5e-05 | -0.3 | -7.5e-05 | -7.5e-05 | 0 | -7.5e-05 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 04:00:00.000 | -0.5 | -0.000125 | 0 | 0 | -6.25e-05 | 0 | -6.25e-05 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 04:15:00.000 | -1 | -0.00025 | 0 | 0 | -0.000125 | 0 | -0.000125 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 04:30:00.000 | -0.6 | -0.00015 | -0.4 | -0.0001 | -0.000125 | 0 | -0.000125 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 04:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 05:00:00.000 | -1.1 | -0.000275 | -1 | -0.00025 | -0.0002625 | 0 | -0.0002625 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 05:15:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 05:30:00.000 | -0.3 | -7.5e-05 | 0 | 0 | -3.75e-05 | 0 | -3.75e-05 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 05:45:00.000 | -0.1 | -2.5e-05 | 0 | 0 | -1.25e-05 | 0 | -1.25e-05 | 0 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 06:00:00.000 | 0.3 | 7.5e-05 | 0.5 | 0.000125 | 0.0001 | 0 | 0.0001 | 0.5 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 06:15:00.000 | 8.1 | 0.002025 | 8.5 | 0.002125 | 0.002075 | 0 | 0.002075 | 0.048193 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 06:30:00.000 | 31.6 | 0.0079 | 32.3 | 0.008075 | 0.0079875 | 0 | 0.0079875 | 0.021909 | 31262.5 | 31262.5 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 06:45:00.000 | 90.6 | 0.02265 | 93.4 | 0.02335 | 0.023 | 92 | 0.02335 | 0.030435 | 31262.5 | 31262.7 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 07:00:00.000 | 100.8 | 0.0252 | 103.6 | 0.0259 | 0.02555 | 102.2 | 0.0259 | 0.027397 | 31262.7 | 31262.9 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 07:15:00.000 | 88.6 | 0.02215 | 90 | 0.0225 | 0.022325 | 89.3 | 0.0225 | 0.015677 | 31262.9 | 31263.2 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 07:30:00.000 | 80.7 | 0.020175 | 81.5 | 0.020375 | 0.020275 | 81.1 | 0.020375 | 0.0098644 | 31263.2 | 31263.4 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 07:45:00.000 | 74.1 | 0.018525 | 74.9 | 0.018725 | 0.018625 | 74.5 | 0.018725 | 0.010738 | 31263.4 | 31263.6 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 08:00:00.000 | 117.7 | 0.029425 | 119.6 | 0.0299 | 0.029663 | 118.65 | 0.0299 | 0.016013 | 31263.6 | 31263.9 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 08:15:00.000 | 97.4 | 0.02435 | 98 | 0.0245 | 0.024425 | 97.7 | 0.0245 | 0.0061412 | 31263.9 | 31264.2 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 08:30:00.000 | 70.1 | 0.017525 | 70.9 | 0.017725 | 0.017625 | 70.5 | 0.017725 | 0.011348 | 31264.2 | 31264.4 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 08:45:00.000 | 50.3 | 0.012575 | 49.2 | 0.0123 | 0.012438 | 0 | 0.012438 | 0.022111 | 31264.4 | 31264.6 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 09:00:00.000 | 62 | 0.0155 | 62 | 0.0155 | 0.0155 | 62 | 0.0155 | 0 | 31264.6 | 31264.8 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 09:15:00.000 | 100.9 | 0.025225 | 102.5 | 0.025625 | 0.025425 | 101.7 | 0.025625 | 0.015733 | 31264.8 | 31265 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 09:30:00.000 | 179.6 | 0.0449 | 177 | 0.04425 | 0.044575 | 178.3 | 0.0449 | 0.014582 | 31265 | 31265.4 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 09:45:00.000 | 872.3 | 0.21807 | 872.7 | 0.21818 | 0.21813 | 872.5 | 0.21818 | 0.00045845 | 31265.4 | 31266.9 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 10:00:00.000 | 632.7 | 0.15818 | 661.1 | 0.16528 | 0.16173 | 646.9 | 0.16528 | 0.043902 | 31266.9 | 31269 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 10:15:00.000 | 926.3 | 0.23157 | 813.5 | 0.20338 | 0.21747 | 869.9 | 0.23157 | 0.12967 | 31269 | 31270.8 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 10:30:00.000 | 472.7 | 0.11818 | 449.2 | 0.1123 | 0.11524 | 460.95 | 0.11818 | 0.050982 | 31270.8 | 31272.4 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 10:45:00.000 | 581.3 | 0.14532 | 542.8 | 0.1357 | 0.14051 | 562.05 | 0.14532 | 0.068499 | 31272.4 | 31273.8 | 1400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 11:00:00.000 | 387.6 | 0.0969 | 409.1 | 0.10228 | 0.099587 | 398.35 | 0.10228 | 0.053973 | 31273.8 | 31274.9 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 11:15:00.000 | 316.2 | 0.07905 | 303.1 | 0.075775 | 0.077412 | 309.65 | 0.07905 | 0.042306 | 31274.9 | 31275.8 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 11:30:00.000 | 723.8 | 0.18095 | 755.4 | 0.18885 | 0.1849 | 739.6 | 0.18885 | 0.042726 | 31275.8 | 31277 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 11:45:00.000 | 1075.9 | 0.26898 | 1035.8 | 0.25895 | 0.26396 | 1055.85 | 0.26898 | 0.037979 | 31277 | 31278.3 | 1300 | 0.2189 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 0.56031
2026-05-17 | 12:00:00.000 | 1081 | 0.27025 | 1046.1 | 0.26152 | 0.26589 | 1063.55 | 0.27025 | 0.032815 | 31278.3 | 31278.9 | 600 | 0.2189 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 0.56031
2026-05-17 | 12:15:00.000 | 592.1 | 0.14803 | 512.5 | 0.12812 | 0.13808 | 552.3 | 0.14803 | 0.14412 | 31278.9 | 31279.6 | 700 | 0.2189 | 25.0626 | 25.0626 | 25.0626 | 25.0626 | 25.0626 | 25.0626 | 25.0626 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 25.0626 | 25.7076 | 26.9978 | 25.0626 | 308.4916 | 23.1274 | 25.0626 | 25.0626 | 23.1274 | 23.1274 | 26.9978 | 25.0626 | 26.9978 | 26.9978 | 25.0626 | 26.9978 | 26.9978 | 25.3851 | 26.9978 | 23.1274 | 304.6212 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 26.9978 | 23.1274 | 26.6459 | 26.9978 | 23.1274 | 320.1028 | 0.56031
2026-05-17 | 12:30:00.000 | 460.6 | 0.11515 | 403.2 | 0.1008 | 0.10798 | 431.9 | 0.11515 | 0.1329 | 31279.6 | 31280.2 | 600 | 0.2189 | 15.7814 | 15.7814 | 15.7814 | 15.7814 | 15.7814 | 15.7814 | 15.7814 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 15.7814 | 16.2859 | 17.2948 | 15.7814 | 195.4303 | 14.2681 | 15.7814 | 15.7814 | 14.2681 | 14.2681 | 17.2948 | 15.7814 | 17.2948 | 17.2948 | 15.7814 | 17.2948 | 17.2948 | 16.0336 | 17.2948 | 14.2681 | 192.4037 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 17.2948 | 14.2681 | 17.0196 | 17.2948 | 14.2681 | 204.5104 | 0.56031
2026-05-17 | 12:45:00.000 | 1156 | 0.289 | 1095.8 | 0.27395 | 0.28147 | 1125.9 | 0.289 | 0.053468 | 31280.2 | 31280.8 | 600 | 0.2189 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 0.56031
2026-05-17 | 13:00:00.000 | 628.7 | 0.15718 | 614.6 | 0.15365 | 0.15541 | 621.65 | 0.15718 | 0.022682 | 31280.8 | 31281.4 | 600 | 0.2189 | 30.4085 | 30.4085 | 30.4085 | 30.4085 | 30.4085 | 30.4085 | 30.4085 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 30.4085 | 31.1345 | 32.5867 | 30.4085 | 373.6145 | 28.2303 | 30.4085 | 30.4085 | 28.2303 | 28.2303 | 32.5867 | 30.4085 | 32.5867 | 32.5867 | 30.4085 | 32.5867 | 32.5867 | 30.7715 | 32.5867 | 28.2303 | 369.2581 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 32.5867 | 28.2303 | 32.1906 | 32.5867 | 28.2303 | 386.6837 | 0.56031
2026-05-17 | 13:15:00.000 | 1029.1 | 0.25727 | 917.4 | 0.22935 | 0.24331 | 973.25 | 0.25727 | 0.11477 | 31281.4 | 31282.1 | 700 | 0.2189 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 0.56031
2026-05-17 | 13:30:00.000 | 931.3 | 0.23282 | 937.6 | 0.2344 | 0.23361 | 934.45 | 0.2344 | 0.0067419 | 31282.1 | 31282.7 | 600 | 0.2189 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 51.2467 | 52.568 | 52.568 | 51.2467 | 51.2467 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.2377 | 52.568 | 51.2467 | 626.8522 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 51.2467 | 52.4479 | 52.568 | 51.2467 | 629.4947 | 0.56031
2026-05-17 | 13:45:00.000 | 1088.3 | 0.27208 | 1005.4 | 0.25135 | 0.26171 | 1046.85 | 0.27208 | 0.07919 | 31282.7 | 31283.3 | 600 | 0.2189 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 52.568 | 630.816 | 0.56031
2026-05-17 | 14:00:00.000 | 1004.9 | 0.25122 | 833.6 | 0.2084 | 0.22981 | 919.25 | 0.25122 | 0.18635 | 31283.3 | 31283.8 | 500 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 67.5843 | 70.024 | 70.024 | 67.5843 | 67.5843 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 69.4141 | 70.024 | 67.5843 | 832.9688 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 67.5843 | 69.8022 | 70.024 | 67.5843 | 837.8483 | 0.56031
2026-05-17 | 14:15:00.000 | 1050.1 | 0.26252 | 1025.9 | 0.25648 | 0.2595 | 1038 | 0.26252 | 0.023314 | 31283.8 | 31283.8 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 0.56031
2026-05-17 | 14:30:00.000 | 1057.3 | 0.26432 | 1042.8 | 0.2607 | 0.26251 | 1050.05 | 0.26432 | 0.013809 | 31283.8 | 31283.8 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 0.56031
2026-05-17 | 14:45:00.000 | 951.5 | 0.23788 | 917.6 | 0.2294 | 0.23364 | 934.55 | 0.23788 | 0.036274 | 31283.8 | 31283.8 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 68.7101 | 70.024 | 70.024 | 68.7101 | 68.7101 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 69.6955 | 70.024 | 68.7101 | 836.3463 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 68.7101 | 69.9046 | 70.024 | 68.7101 | 838.9741 | 0.56031
2026-05-17 | 15:00:00.000 | 966.5 | 0.24163 | 1026.9 | 0.25673 | 0.24918 | 996.7 | 0.25673 | 0.0606 | 31283.8 | 31283.8 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 0.56031
2026-05-17 | 15:15:00.000 | 966.3 | 0.24157 | 987.6 | 0.2469 | 0.24424 | 976.95 | 0.2469 | 0.021803 | 31283.8 | 31283.8 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 0.56031
2026-05-17 | 15:30:00.000 | 604.7 | 0.15118 | 605.4 | 0.15135 | 0.15126 | 605.05 | 0.15135 | 0.0011569 | 31283.8 | 31284 | 200 | 0.4105 | 13.8008 | 13.8008 | 13.8008 | 13.8008 | 13.8008 | 13.8008 | 13.8008 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 13.8008 | 14.5075 | 15.9209 | 13.8008 | 174.0903 | 11.6808 | 13.8008 | 13.8008 | 11.6808 | 11.6808 | 15.9209 | 13.8008 | 15.9209 | 15.9209 | 13.8008 | 15.9209 | 15.9209 | 14.1542 | 15.9209 | 11.6808 | 169.8502 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 15.9209 | 11.6808 | 15.5354 | 15.9209 | 11.6808 | 186.8105 | 0.56031
2026-05-17 | 15:45:00.000 | 960.4 | 0.2401 | 852.7 | 0.21318 | 0.22664 | 906.55 | 0.2401 | 0.1188 | 31284 | 31285.1 | 1100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 16:00:00.000 | 544 | 0.136 | 563.4 | 0.14085 | 0.13843 | 553.7 | 0.14085 | 0.035037 | 31285.1 | 31286.6 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 16:15:00.000 | 789.7 | 0.19743 | 757.8 | 0.18945 | 0.19344 | 773.75 | 0.19743 | 0.041228 | 31286.6 | 31288.1 | 1500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 16:30:00.000 | 965.1 | 0.24128 | 946.6 | 0.23665 | 0.23896 | 955.85 | 0.24128 | 0.019355 | 31288.1 | 31290.2 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 16:45:00.000 | 812 | 0.203 | 846 | 0.2115 | 0.20725 | 829 | 0.2115 | 0.041013 | 31290.2 | 31292.4 | 2200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 17:00:00.000 | 927.5 | 0.23187 | 888.1 | 0.22203 | 0.22695 | 907.8 | 0.23187 | 0.043402 | 31292.4 | 31294.5 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 17:15:00.000 | 894.2 | 0.22355 | 882.6 | 0.22065 | 0.2221 | 888.4 | 0.22355 | 0.013057 | 31294.5 | 31296.5 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 17:30:00.000 | 863.8 | 0.21595 | 901.4 | 0.22535 | 0.22065 | 882.6 | 0.22535 | 0.042601 | 31296.5 | 31298.8 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 17:45:00.000 | 761.9 | 0.19048 | 824 | 0.206 | 0.19824 | 792.95 | 0.206 | 0.078315 | 31298.8 | 31300.9 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 18:00:00.000 | 654.6 | 0.16365 | 727.9 | 0.18197 | 0.17281 | 691.25 | 0.18197 | 0.10604 | 31300.9 | 31302.7 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 18:15:00.000 | 547.4 | 0.13685 | 628.7 | 0.15718 | 0.14701 | 588.05 | 0.15718 | 0.13825 | 31302.7 | 31304.3 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 18:30:00.000 | 443.9 | 0.11097 | 519.7 | 0.12993 | 0.12045 | 481.8 | 0.12993 | 0.15733 | 31304.3 | 31305.6 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 18:45:00.000 | 344.9 | 0.086225 | 415.7 | 0.10393 | 0.095075 | 380.3 | 0.10393 | 0.18617 | 31305.6 | 31306.6 | 1000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 19:00:00.000 | 226 | 0.0565 | 286.6 | 0.07165 | 0.064075 | 256.3 | 0.07165 | 0.23644 | 31306.6 | 31307.3 | 700 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 19:15:00.000 | 122.6 | 0.03065 | 164.9 | 0.041225 | 0.035938 | 143.75 | 0.041225 | 0.29426 | 31307.3 | 31307.7 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 19:30:00.000 | 80.6 | 0.02015 | 114.5 | 0.028625 | 0.024387 | 97.55 | 0.028625 | 0.34751 | 31307.7 | 31308 | 300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 19:45:00.000 | 42.6 | 0.01065 | 64.4 | 0.0161 | 0.013375 | 53.5 | 0.0161 | 0.40748 | 31308 | 31308.1 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 20:00:00.000 | 20.8 | 0.0052 | 23.1 | 0.005775 | 0.0054875 | 0 | 0.0054875 | 0.10478 | 31308.1 | 31308.2 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 20:15:00.000 | 7.3 | 0.001825 | 7.9 | 0.001975 | 0.0019 | 0 | 0.0019 | 0.078947 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 20:30:00.000 | -0.3 | -7.5e-05 | 0.1 | 2.5e-05 | -2.5e-05 | 0 | -2.5e-05 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 20:45:00.000 | -2 | -0.0005 | -1.6 | -0.0004 | -0.00045 | 0 | -0.00045 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 21:00:00.000 | -1.9 | -0.000475 | -1.6 | -0.0004 | -0.0004375 | 0 | -0.0004375 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 21:15:00.000 | -1.6 | -0.0004 | -1.5 | -0.000375 | -0.0003875 | 0 | -0.0003875 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 21:30:00.000 | -2.4 | -0.0006 | -2.6 | -0.00065 | -0.000625 | 0 | -0.000625 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 21:45:00.000 | -2.2 | -0.00055 | -2.4 | -0.0006 | -0.000575 | 0 | -0.000575 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 22:00:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 22:15:00.000 | -1.7 | -0.000425 | -2 | -0.0005 | -0.0004625 | 0 | -0.0004625 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 22:30:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 22:45:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 23:00:00.000 | -3 | -0.00075 | -2.3 | -0.000575 | -0.0006625 | 0 | -0.0006625 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 23:15:00.000 | -3 | -0.00075 | -2.8 | -0.0007 | -0.000725 | 0 | -0.000725 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 23:30:00.000 | -3 | -0.00075 | -2.5 | -0.000625 | -0.0006875 | 0 | -0.0006875 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
2026-05-17 | 23:45:00.000 | -2.8 | -0.0007 | -2 | -0.0005 | -0.0006 | 0 | -0.0006 | 0 | 31308.2 | 31308.2 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56031
PR for each inverter |  |  | 7.665 |  | 7.5861 | 7.6255 |  | 7.8657 |  |  |  | 45700 |  | 0.76185 | 0.76768 | 0.76876 | 0.77536 | 0.77775 | 0.77111 | 0.77487 | 0.80897 | 0.80134 | 0.78909 | 0.80284 | 0.82 | #DIV/0! | #DIV/0! | #DIV/0! | 9878.2507 | 0.80187 | 0.77099 | 0.77155 | 0.7963 | 0.83535 | 0.79214 | 0.8271 | 0.80549 | 0.80757 | 0.82612 | 0.79061 | 0.80544 |  |  |  | 9847.5325 | 0.81077 | 0.80073 | 0.76714 | 0.79379 | 0.78259 | 0.75264 | 0.76032 | 0.74877 | 0.75841 | 0.79995 | 0.79547 | 0.79703 | #DIV/0! | #DIV/0! | #DIV/0! | 9919.6566 |  | 0.78938 |  | #DIV/0! | #DIV/0! | 7.9583e-06
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-17 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0 | 0 | 0.6 | 0.3 | 0 | 0.6 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0.1 | 0.54 | 1.1 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 1.3 | 0
2026-05-17 | 06:30:00.000 | 6.3 | 6.5 | 6 | 6.1 | 6.8 | 6.5 | 5.6 | 7.7 | 7.9 | 7.1 | 7.4 | 7.1 | 6.75 | 7.9 | 5.6 | 6.1 | 7.8 | 6.9 | 5.6 | 7.3 | 7.5 | 7.9 | 8.2 | 8.2 | 7.2 | 7.4 | 8.6 | 7.3917 | 8.6 | 5.6 | 8.1 | 7.1 | 6.9 | 7.8 | 7.5 | 6.3 | 6.9 | 6.8 | 6.8 | 7.4 | 8 | 6.5 | 7.175 | 8.1 | 6.3
2026-05-17 | 06:45:00.000 | 23.7 | 22.9 | 24.1 | 23.5 | 22.7 | 21.9 | 21.5 | 27.5 | 25.6 | 26.4 | 27.1 | 25.9 | 24.4 | 27.5 | 21.5 | 21.7 | 23.2 | 22 | 21.3 | 23.7 | 26.8 | 27.1 | 27.9 | 28.4 | 26.9 | 26.4 | 28.2 | 25.3 | 28.4 | 21.3 | 27.7 | 26.1 | 24.4 | 27.5 | 26.8 | 25.2 | 26.5 | 25.8 | 25.7 | 26.7 | 27.8 | 23.4 | 26.1333 | 27.8 | 23.4
2026-05-17 | 07:00:00.000 | 27.5 | 27.1 | 27 | 26.2 | 25.8 | 25 | 24.7 | 32.1 | 31.2 | 30 | 31.2 | 28.7 | 28.0417 | 32.1 | 24.7 | 24.6 | 25.8 | 24.9 | 24.3 | 27.4 | 30.7 | 31.4 | 32.4 | 32.9 | 31.2 | 30.5 | 31.3 | 28.95 | 32.9 | 24.3 | 31.2 | 29.4 | 27 | 31 | 30.1 | 26.6 | 29 | 28.5 | 28.4 | 30.6 | 31.1 | 25.3 | 29.0167 | 31.2 | 25.3
2026-05-17 | 07:15:00.000 | 24.4 | 24.3 | 24 | 24.4 | 24.2 | 23.6 | 23.8 | 30.4 | 29.4 | 27.9 | 29.1 | 28.1 | 26.1333 | 30.4 | 23.6 | 23.6 | 24.4 | 23.8 | 23.1 | 26 | 28.9 | 29.3 | 30.3 | 30.3 | 28.9 | 28.5 | 30.2 | 27.275 | 30.3 | 23.1 | 29.5 | 28.6 | 25.7 | 28.9 | 28.1 | 25.1 | 25.9 | 25.3 | 25.6 | 29.2 | 28.8 | 22.9 | 26.9667 | 29.5 | 22.9
2026-05-17 | 07:30:00.000 | 22.2 | 22.3 | 22.2 | 22.8 | 22.6 | 22 | 22.3 | 28.1 | 27.3 | 25.8 | 27.1 | 26.3 | 24.25 | 28.1 | 22 | 22 | 22.7 | 22.2 | 21.5 | 24.3 | 27 | 27.3 | 28.1 | 28.2 | 26.9 | 26.5 | 28 | 25.3917 | 28.2 | 21.5 | 27.5 | 26.7 | 24 | 27 | 26.2 | 23.5 | 24 | 23.2 | 23.5 | 27.2 | 26.8 | 21.4 | 25.0833 | 27.5 | 21.4
2026-05-17 | 07:45:00.000 | 20.4 | 20.5 | 20.5 | 21 | 20.9 | 20.3 | 20.6 | 25.9 | 25.2 | 23 | 25 | 24.3 | 22.3 | 25.9 | 20.3 | 20.4 | 21 | 20.5 | 19.8 | 22.4 | 24.9 | 25.2 | 26 | 26 | 24.8 | 24.4 | 25.9 | 23.4417 | 26 | 19.8 | 25.4 | 24.8 | 22.3 | 25 | 24.3 | 21.7 | 22.2 | 21.5 | 21.7 | 25.2 | 24.8 | 19.8 | 23.225 | 25.4 | 19.8
2026-05-17 | 08:00:00.000 | 32.9 | 33.1 | 33.2 | 34 | 33.8 | 33 | 33.7 | 42 | 40.9 | 38.8 | 40.7 | 39.6 | 36.3083 | 42 | 32.9 | 33.3 | 34.3 | 33.6 | 32.5 | 36.6 | 40.8 | 41.2 | 42.7 | 42.6 | 40.7 | 40.1 | 42.6 | 38.4167 | 42.7 | 32.5 | 41.1 | 40.3 | 36.1 | 40.2 | 39.1 | 34.9 | 35.6 | 34.5 | 35 | 40.7 | 39.9 | 31.6 | 37.4167 | 41.1 | 31.6
2026-05-17 | 08:15:00.000 | 28.4 | 28.4 | 28.5 | 29.2 | 29 | 28.3 | 28.9 | 36 | 34.9 | 33.1 | 34.7 | 33.8 | 31.1 | 36 | 28.3 | 28.5 | 29.4 | 28.7 | 27.7 | 31.1 | 34.8 | 35.1 | 36.3 | 36.1 | 34.4 | 33.8 | 35.9 | 32.65 | 36.3 | 27.7 | 34.9 | 34.3 | 30.8 | 34.3 | 33.5 | 29.9 | 30.7 | 29.6 | 30 | 34.7 | 34.1 | 27.3 | 32.0083 | 34.9 | 27.3
2026-05-17 | 08:30:00.000 | 21 | 21 | 21 | 21.6 | 21.5 | 20.9 | 21.4 | 26.8 | 26 | 24.5 | 25.7 | 25.1 | 23.0417 | 26.8 | 20.9 | 21.2 | 21.9 | 21.4 | 20.5 | 23.1 | 25.9 | 26.2 | 27.1 | 26.8 | 25.6 | 25.2 | 26.8 | 24.3083 | 27.1 | 20.5 | 25.7 | 25.4 | 22.7 | 25.2 | 24.7 | 22 | 22.6 | 21.8 | 22.1 | 25.6 | 25.1 | 20 | 23.575 | 25.7 | 20
2026-05-17 | 08:45:00.000 | 15.7 | 15.6 | 15.5 | 16 | 15.8 | 15.5 | 15.9 | 19.8 | 19.1 | 18 | 18.8 | 18.4 | 17.0083 | 19.8 | 15.5 | 15.7 | 16.3 | 15.8 | 15.1 | 17 | 19 | 19.1 | 19.7 | 19.5 | 18.5 | 18.3 | 19.4 | 17.7833 | 19.7 | 15.1 | 18.5 | 18.4 | 16.4 | 18.2 | 17.8 | 16 | 16.5 | 15.8 | 16 | 18.5 | 18.2 | 14.6 | 17.075 | 18.5 | 14.6
2026-05-17 | 09:00:00.000 | 20.5 | 20.3 | 20 | 20.5 | 20.4 | 19.9 | 20.5 | 25.3 | 24.4 | 23 | 23.9 | 23.6 | 21.8583 | 25.3 | 19.9 | 20.3 | 21.1 | 20.5 | 19.4 | 21.9 | 24.2 | 24.2 | 25.1 | 24.8 | 23.6 | 23.5 | 24.8 | 22.7833 | 25.1 | 19.4 | 24.1 | 24 | 21.7 | 23.7 | 23.2 | 21.1 | 21.8 | 21 | 21.2 | 24.1 | 23.8 | 19.4 | 22.425 | 24.1 | 19.4
2026-05-17 | 09:15:00.000 | 32.4 | 32 | 31.8 | 32.7 | 32.6 | 31.6 | 32.5 | 40.3 | 38.7 | 36.6 | 38 | 37.3 | 34.7083 | 40.3 | 31.6 | 32.2 | 33.4 | 32.5 | 30.9 | 34.7 | 38.4 | 38.3 | 39.8 | 39.4 | 37.6 | 37.2 | 39.4 | 36.15 | 39.8 | 30.9 | 38.6 | 38.1 | 34.4 | 37.6 | 36.9 | 33.5 | 34.8 | 33.4 | 33.8 | 38.5 | 37.9 | 31.1 | 35.7167 | 38.6 | 31.1
2026-05-17 | 09:30:00.000 | 51.1 | 51.1 | 49.9 | 53.2 | 52.1 | 51.1 | 54.1 | 63.5 | 61.5 | 58.4 | 60.4 | 61.3 | 55.6417 | 63.5 | 49.9 | 53.7 | 55.9 | 54 | 52.1 | 59.1 | 63.7 | 61 | 64.6 | 62.7 | 59.7 | 60.7 | 64.3 | 59.2917 | 64.6 | 52.1 | 61.5 | 60 | 52.6 | 54.3 | 57.6 | 51.7 | 54.5 | 51.9 | 52.2 | 54.9 | 60.4 | 47.5 | 54.925 | 61.5 | 47.5
2026-05-17 | 09:45:00.000 | 232.5 | 235.8 | 239 | 243 | 243.5 | 239.3 | 242.2 | 269.3 | 264.8 | 264.2 | 267.3 | 265.6 | 250.5417 | 269.3 | 232.5 | 232.1 | 246.2 | 233 | 234.9 | 256.5 | 268.2 | 263.5 | 271.8 | 270.5 | 263.7 | 262.4 | 266.4 | 255.7667 | 271.8 | 232.1 | 270.8 | 265.6 | 255.1 | 265.3 | 264.7 | 248.6 | 255.6 | 246.1 | 248.6 | 268.9 | 256.5 | 227.2 | 256.0833 | 270.8 | 227.2
2026-05-17 | 10:00:00.000 | 167.6 | 181.5 | 193.5 | 208 | 210.1 | 212.2 | 216.5 | 210.1 | 218 | 213.3 | 221.9 | 221.1 | 206.15 | 221.9 | 167.6 | 209.9 | 207.4 | 215.3 | 208.4 | 222 | 221 | 235 | 249.8 | 250.1 | 242 | 237.4 | 241.5 | 228.3167 | 250.1 | 207.4 | 214.6 | 209.9 | 197.9 | 208.7 | 205.3 | 193.6 | 180.9 | 174.1 | 179.4 | 199.1 | 199.3 | 155 | 193.15 | 214.6 | 155
2026-05-17 | 10:15:00.000 | 226.5 | 232.7 | 228.5 | 224.9 | 216.9 | 207.5 | 208.9 | 253.3 | 249.7 | 242.3 | 243.8 | 235 | 230.8333 | 253.3 | 207.5 | 205.7 | 206.9 | 204 | 197.7 | 205 | 242.1 | 242.4 | 244.3 | 243.9 | 241.3 | 237.6 | 245.1 | 226.3333 | 245.1 | 197.7 | 231 | 220.1 | 203.8 | 202.1 | 186.3 | 186.2 | 191.3 | 194.7 | 198.7 | 209.9 | 222.3 | 176.9 | 201.9417 | 231 | 176.9
2026-05-17 | 10:30:00.000 | 125.6 | 122.7 | 123.3 | 119.5 | 125.7 | 121.7 | 113.7 | 150.6 | 140.6 | 141.9 | 144.3 | 136.5 | 130.5083 | 150.6 | 113.7 | 119.8 | 124.6 | 118 | 114.9 | 123.8 | 141.6 | 140.7 | 143.5 | 142.1 | 134.7 | 128.1 | 141.8 | 131.1333 | 143.5 | 114.9 | 150.6 | 143.7 | 128.8 | 141.8 | 138.2 | 123.4 | 130.5 | 126.1 | 126.9 | 145.3 | 147.1 | 120.7 | 135.2583 | 150.6 | 120.7
2026-05-17 | 10:45:00.000 | 140.1 | 136.3 | 145.9 | 129 | 139.1 | 135.3 | 140.1 | 175.1 | 178.8 | 167.9 | 169.4 | 164.8 | 151.8167 | 178.8 | 129 | 150.1 | 146.7 | 150.9 | 142.5 | 158.6 | 165.9 | 151.3 | 163.5 | 163.2 | 156.9 | 156.3 | 156.7 | 155.2167 | 165.9 | 142.5 | 161 | 158.7 | 147.7 | 167 | 165.4 | 161.4 | 163.4 | 155.1 | 154.9 | 165.2 | 157 | 190.3 | 162.2583 | 190.3 | 147.7
2026-05-17 | 11:00:00.000 | 109.6 | 102.6 | 94.5 | 88.2 | 86.8 | 82.8 | 83 | 122.9 | 110.8 | 105.1 | 109.2 | 105.6 | 100.0917 | 122.9 | 82.8 | 81.5 | 83.5 | 81.1 | 78.5 | 87.6 | 115.1 | 115.7 | 118 | 119.3 | 113.8 | 109.9 | 120.9 | 102.075 | 120.9 | 78.5 | 127 | 125.2 | 114.7 | 129 | 133 | 126.3 | 143.2 | 121.3 | 121.8 | 134 | 126.4 | 160.9 | 130.2333 | 160.9 | 114.7
2026-05-17 | 11:15:00.000 | 87.1 | 88.5 | 90.3 | 93.8 | 96 | 98.3 | 103.9 | 108.5 | 106.1 | 102 | 110.8 | 105.4 | 99.225 | 110.8 | 87.1 | 98.3 | 102.4 | 102.9 | 99.9 | 115.7 | 105.3 | 107 | 114.8 | 117.4 | 113.6 | 114.6 | 117.9 | 109.15 | 117.9 | 98.3 | 103.3 | 100.8 | 91 | 100.8 | 98.2 | 86.7 | 88.6 | 85.6 | 86.8 | 100.5 | 99.4 | 79.7 | 93.45 | 103.3 | 79.7
2026-05-17 | 11:30:00.000 | 164.5 | 170.2 | 168.7 | 175.9 | 183.6 | 191.4 | 189.6 | 186.6 | 191.3 | 194.7 | 201.7 | 199.5 | 184.8083 | 201.7 | 164.5 | 192.5 | 195.4 | 200.9 | 198.8 | 205.3 | 191 | 208 | 207.8 | 208.7 | 207.8 | 206.4 | 205.8 | 202.3667 | 208.7 | 191 | 198.7 | 198.1 | 191.6 | 197.3 | 191.8 | 185.3 | 194.1 | 180.4 | 179.7 | 189.4 | 192.4 | 207.6 | 192.2 | 207.6 | 179.7
2026-05-17 | 11:45:00.000 | 70.9 | 70.5 | 70.5 | 71.1 | 70.4 | 70.6 | 70.9 | 71.1 | 70.4 | 71.2 | 70.7 | 70.7 | 70.75 | 71.2 | 70.4 | 70.6 | 70.7 | 70.5 | 69.8 | 71 | 71 | 70.5 | 70.3 | 70.2 | 71.1 | 71 | 70.2 | 70.575 | 71.1 | 69.8 | 71.2 | 71.1 | 71.3 | 71.3 | 71.4 | 70.6 | 70.4 | 70.4 | 70.3 | 70.3 | 70.3 | 71.3 | 70.825 | 71.4 | 70.3
2026-05-17 | 12:00:00.000 | 70.9 | 70.5 | 70.5 | 70.3 | 70.4 | 70.8 | 70.4 | 71.1 | 70.3 | 70 | 70.7 | 70.9 | 70.5667 | 71.1 | 70 | 71 | 71.1 | 70.1 | 70.2 | 70.5 | 70.8 | 70.7 | 70.5 | 70.4 | 70.4 | 69.9 | 70.4 | 70.5 | 71.1 | 69.9 | 71.1 | 68.6 | 71.3 | 71.3 | 71.4 | 70.6 | 70.4 | 70.3 | 70.2 | 67.9 | 70.3 | 71.3 | 70.3917 | 71.4 | 67.9
2026-05-17 | 12:15:00.000 | 68.9 | 68.9 | 68.6 | 66.7 | 67.1 | 68.7 | 68.9 | 71.1 | 70.3 | 69.8 | 70.6 | 70.8 | 69.2 | 71.1 | 66.7 | 68.7 | 69.6 | 68.6 | 68 | 70.2 | 70.5 | 70.6 | 70.3 | 70.3 | 70.1 | 69.6 | 70.6 | 69.7583 | 70.6 | 68 | 70.7 | 71 | 70.6 | 70.9 | 71.2 | 70.1 | 70.1 | 69.8 | 69.6 | 70.2 | 70.4 | 69.3 | 70.325 | 71.2 | 69.3
2026-05-17 | 12:30:00.000 | 70.8 | 70.9 | 70.6 | 71 | 70.6 | 70.7 | 70.7 | 70.3 | 70.3 | 67.6 | 70.7 | 68.3 | 70.2083 | 71 | 67.6 | 70.8 | 70.9 | 70.7 | 70.7 | 70.3 | 70.8 | 70 | 70.4 | 70.6 | 70.6 | 70 | 70.8 | 70.55 | 70.9 | 70 | 70.8 | 71.1 | 70.5 | 70.7 | 70.4 | 70.3 | 70.3 | 70.2 | 70.5 | 70.1 | 70.4 | 70.4 | 70.475 | 71.1 | 70.1
2026-05-17 | 12:45:00.000 | 70.1 | 70.5 | 70.8 | 70.2 | 71 | 70.3 | 70 | 70.4 | 70.5 | 70.3 | 70.9 | 71 | 70.5 | 71 | 70 | 70.3 | 70.4 | 70.2 | 70.1 | 70.3 | 71 | 69.5 | 70.6 | 70.5 | 71 | 70.1 | 70.9 | 70.4083 | 71 | 69.5 | 71 | 67.8 | 70.7 | 70.8 | 70.3 | 70.2 | 70.6 | 70.2 | 70.8 | 70.4 | 70.6 | 70.8 | 70.35 | 71 | 67.8
2026-05-17 | 13:00:00.000 | 70 | 70 | 70.6 | 70.4 | 70.6 | 70 | 69.7 | 70.1 | 70.3 | 70.1 | 70.7 | 70.9 | 70.2833 | 70.9 | 69.7 | 69.8 | 70.2 | 70.1 | 70.1 | 69.6 | 70.8 | 69.3 | 70.3 | 70.3 | 70.6 | 69.9 | 70.7 | 70.1417 | 70.8 | 69.3 | 70.8 | 70 | 70.5 | 70.4 | 70.1 | 70 | 70.4 | 70 | 70.6 | 70.1 | 70.4 | 70.6 | 70.325 | 70.8 | 70
2026-05-17 | 13:15:00.000 | 70.1 | 70 | 70.8 | 70.7 | 70.8 | 70.1 | 69.9 | 70.2 | 70.3 | 70.1 | 70.7 | 70.9 | 70.3833 | 70.9 | 69.9 | 69.5 | 70.9 | 70.6 | 70.2 | 69.8 | 70.8 | 68.9 | 70.4 | 70.3 | 70.1 | 69.9 | 70.7 | 70.175 | 70.9 | 68.9 | 70.5 | 70.1 | 70.6 | 70.5 | 67.9 | 70.2 | 70.6 | 67.8 | 70.8 | 70.3 | 70.5 | 70.9 | 70.0583 | 70.9 | 67.8
2026-05-17 | 13:30:00.000 | 70.7 | 70.1 | 70.7 | 70.8 | 70.8 | 70.2 | 70 | 70.3 | 70.4 | 70.2 | 68.3 | 71.1 | 70.3 | 71.1 | 68.3 | 67.4 | 70.3 | 70.1 | 70.1 | 69.3 | 70.9 | 69 | 70.5 | 70.4 | 70.2 | 70 | 70.8 | 69.9167 | 70.9 | 67.4 | 68.9 | 70.2 | 70.7 | 70.5 | 70.3 | 70.2 | 71 | 70.2 | 70.8 | 70.3 | 70.6 | 70.4 | 70.3417 | 71 | 68.9
2026-05-17 | 13:45:00.000 | 70.6 | 70 | 70.3 | 70.7 | 70.7 | 70.2 | 69.9 | 70.3 | 70.4 | 70.1 | 70.8 | 70.9 | 70.4083 | 70.9 | 69.9 | 69.7 | 70.1 | 69.8 | 69.4 | 69.2 | 70.9 | 68.9 | 70.5 | 70.4 | 70.3 | 69.9 | 68.6 | 69.8083 | 70.9 | 68.6 | 69.7 | 70 | 70.5 | 70.4 | 70.2 | 70.1 | 71 | 70.1 | 70.6 | 70.1 | 70.5 | 70.5 | 70.3083 | 71 | 69.7
2026-05-17 | 14:00:00.000 | 20.9 | 20.5 | 21.8 | 20.6 | 21.3 | 21.8 | 20 | 22.1 | 22.2 | 21 | 21.6 | 20.2 | 21.1667 | 22.2 | 20 | 20 | 22.2 | 20.1 | 21.7 | 21.5 | 19.9 | 21 | 20.6 | 20.6 | 20.9 | 21.3 | 21.3 | 20.925 | 22.2 | 19.9 | 20.6 | 21.6 | 20.3 | 22.3 | 22 | 19.9 | 22.1 | 21.2 | 21 | 20.3 | 21.5 | 21.1 | 21.1583 | 22.3 | 19.9
2026-05-17 | 14:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-17 | 14:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-17 | 14:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-17 | 15:00:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-17 | 15:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-17 | 15:30:00.000 | 69.6 | 67.9 | 67.7 | 66.3 | 65.2 | 64.9 | 66.6 | 74.2 | 72.1 | 71.6 | 73.6 | 71.9 | 69.3 | 74.2 | 64.9 | 67 | 64.6 | 66.2 | 62 | 69.8 | 75.1 | 74.7 | 76.3 | 76.2 | 75.8 | 74.7 | 76.3 | 71.5583 | 76.3 | 62 | 79.8 | 76.7 | 75.9 | 80.7 | 77.7 | 79.9 | 78.1 | 75.7 | 68.9 | 74.8 | 75.8 | 71 | 76.25 | 80.7 | 68.9
2026-05-17 | 15:45:00.000 | 154.5 | 160.4 | 153.6 | 148.8 | 148.9 | 150.5 | 147.7 | 161.2 | 157.2 | 152.5 | 151 | 151.6 | 153.1583 | 161.2 | 147.7 | 143.4 | 139.4 | 143.6 | 137.6 | 141.6 | 149 | 143 | 143.6 | 142.1 | 146.9 | 142.3 | 141.1 | 142.8 | 149 | 137.6 | 152.5 | 147.6 | 153.3 | 151.9 | 148.4 | 147.5 | 151.5 | 152.8 | 154.4 | 157.4 | 156.7 | 155.1 | 152.425 | 157.4 | 147.5
2026-05-17 | 16:00:00.000 | 128.1 | 128.4 | 139.6 | 141.2 | 143.1 | 149.5 | 147.8 | 156.6 | 162.5 | 162.5 | 167 | 169.9 | 149.6833 | 169.9 | 128.1 | 150.8 | 153 | 146.3 | 158.6 | 168.9 | 180.2 | 182.1 | 181.5 | 185.2 | 176.4 | 180.6 | 176.8 | 170.0333 | 185.2 | 146.3 | 166 | 174.6 | 150 | 158.1 | 151.1 | 142.8 | 142.3 | 141.8 | 144 | 156 | 156.8 | 125.8 | 150.775 | 174.6 | 125.8
2026-05-17 | 16:15:00.000 | 187.3 | 191.6 | 188.3 | 189.2 | 189.6 | 193.8 | 194.7 | 204.2 | 201.2 | 204.1 | 207.7 | 210.6 | 196.8583 | 210.6 | 187.3 | 196.3 | 199.4 | 207 | 212.2 | 215.5 | 223.8 | 230.2 | 217.6 | 229 | 228.6 | 233.7 | 234.6 | 218.9917 | 234.6 | 196.3 | 215 | 205.5 | 190.6 | 199 | 195.8 | 184.6 | 180.5 | 188.4 | 195.5 | 196.4 | 204.9 | 176.7 | 194.4083 | 215 | 176.7
2026-05-17 | 16:30:00.000 | 235.8 | 240.4 | 243.2 | 255.1 | 254.7 | 249.9 | 247.1 | 259.7 | 261.8 | 253.9 | 266.6 | 256 | 252.0167 | 266.6 | 235.8 | 245.8 | 243.4 | 246.6 | 248.8 | 262.9 | 265.1 | 263.5 | 262.5 | 267 | 247.2 | 270.8 | 272.6 | 258.0167 | 272.6 | 243.4 | 260.6 | 255.6 | 239.8 | 251.3 | 246.4 | 236.8 | 231.7 | 234.8 | 240.2 | 252.4 | 253.5 | 230.2 | 244.4417 | 260.6 | 230.2
2026-05-17 | 16:45:00.000 | 203.3 | 206.6 | 213.8 | 225.2 | 232.6 | 234.8 | 254.1 | 243 | 243.7 | 259 | 264.9 | 253.4 | 236.2 | 264.9 | 203.3 | 251.9 | 246 | 251.9 | 253.6 | 264.6 | 272.7 | 271.4 | 273.2 | 275.6 | 274.6 | 276.1 | 278.9 | 265.875 | 278.9 | 246 | 266 | 249.6 | 225.7 | 227.7 | 212.9 | 191.9 | 190.6 | 196.7 | 206 | 220.2 | 235 | 203.6 | 218.825 | 266 | 190.6
2026-05-17 | 17:00:00.000 | 223.2 | 233.5 | 228.7 | 248 | 240.1 | 224.9 | 224.5 | 261.2 | 247.7 | 237.4 | 242.7 | 222.4 | 236.1917 | 261.2 | 222.4 | 217.5 | 209.5 | 209.9 | 211.6 | 233.1 | 224.3 | 227.5 | 231.3 | 231.6 | 231.2 | 234.4 | 244 | 225.4917 | 244 | 209.5 | 226.5 | 233 | 233.1 | 247.5 | 242.3 | 219.3 | 216.3 | 220.2 | 235.4 | 256.9 | 248.7 | 196.7 | 231.325 | 256.9 | 196.7
2026-05-17 | 17:15:00.000 | 222.2 | 226.3 | 227 | 229.7 | 231.1 | 225.2 | 228.1 | 257.3 | 257.3 | 253.6 | 252.5 | 253.6 | 238.6583 | 257.3 | 222.2 | 223 | 214.4 | 217.5 | 210.9 | 244.8 | 241.5 | 247.9 | 261 | 261.4 | 258 | 255.4 | 262.8 | 241.55 | 262.8 | 210.9 | 265.4 | 261.8 | 249.4 | 263.7 | 263.5 | 247.2 | 247.6 | 237.9 | 240.9 | 247.5 | 258.1 | 228.4 | 250.95 | 265.4 | 228.4
2026-05-17 | 17:30:00.000 | 218 | 221.5 | 222 | 224.9 | 225.6 | 221.9 | 229.1 | 276.9 | 273.1 | 261.8 | 271.2 | 255.8 | 241.8167 | 276.9 | 218 | 217.4 | 211.2 | 213 | 212 | 239.2 | 255.7 | 247.9 | 265.8 | 267.4 | 254.9 | 253.9 | 265.7 | 242.0083 | 267.4 | 211.2 | 279.5 | 275.2 | 251.6 | 276.3 | 268.8 | 244.8 | 251.5 | 232.5 | 247 | 278.4 | 275.7 | 216.7 | 258.1667 | 279.5 | 216.7
2026-05-17 | 17:45:00.000 | 191.9 | 195.3 | 195.3 | 198.2 | 199 | 195.2 | 200.5 | 251.4 | 245.4 | 232.9 | 242.9 | 227.3 | 214.6083 | 251.4 | 191.9 | 191.4 | 186.9 | 187.9 | 185.9 | 211.4 | 230 | 228.5 | 235.4 | 237 | 225 | 222.1 | 233.5 | 214.5833 | 237 | 185.9 | 257.4 | 250.2 | 225.6 | 249.8 | 238.9 | 216.2 | 223 | 214.2 | 220.1 | 255.9 | 249 | 184.1 | 232.0333 | 257.4 | 184.1
2026-05-17 | 18:00:00.000 | 165 | 168 | 167.5 | 170.3 | 171.2 | 167.7 | 168.9 | 220.4 | 214.5 | 203.2 | 213 | 197.7 | 185.6167 | 220.4 | 165 | 164.4 | 161.9 | 162 | 159.3 | 182.8 | 191.4 | 198.2 | 203.7 | 205.5 | 195 | 191.6 | 202.5 | 184.8583 | 205.5 | 159.3 | 225.8 | 220.7 | 196.9 | 208.6 | 206.8 | 186.3 | 192.8 | 185.3 | 191.2 | 225.8 | 217.6 | 170.8 | 202.3833 | 225.8 | 170.8
2026-05-17 | 18:15:00.000 | 138.2 | 140.7 | 140.4 | 142.9 | 139.3 | 137.9 | 137.8 | 187.3 | 175.6 | 171.2 | 174.2 | 167.2 | 154.3917 | 187.3 | 137.8 | 138.4 | 136.6 | 137 | 133.6 | 149.7 | 167 | 167.9 | 172.7 | 173.3 | 163.6 | 159.1 | 169.2 | 155.675 | 173.3 | 133.6 | 192.5 | 189.5 | 166.6 | 182.1 | 174.9 | 157.8 | 163.6 | 157.6 | 162.8 | 194.8 | 184.9 | 140.1 | 172.2667 | 194.8 | 140.1
2026-05-17 | 18:30:00.000 | 111 | 113.1 | 108.8 | 114.5 | 115.6 | 105.4 | 107.8 | 153.1 | 147.8 | 139 | 147.4 | 135.7 | 124.9333 | 153.1 | 105.4 | 110.5 | 109.5 | 110.3 | 106.2 | 123.5 | 133.7 | 135.4 | 139 | 139.3 | 131.2 | 126.5 | 135.2 | 125.025 | 139.3 | 106.2 | 158.1 | 154.8 | 133.8 | 144.6 | 140.1 | 126 | 131 | 126.4 | 131.5 | 160.6 | 144.9 | 116.4 | 139.0167 | 160.6 | 116.4
2026-05-17 | 18:45:00.000 | 84.9 | 86.6 | 82.7 | 87.4 | 88.3 | 84.4 | 81 | 114.9 | 115 | 107.4 | 114.5 | 104 | 95.925 | 115 | 81 | 83.7 | 82.1 | 84.3 | 79.7 | 93.5 | 101.1 | 103 | 105.8 | 105.3 | 98.9 | 94.3 | 101.6 | 94.4417 | 105.8 | 79.7 | 122.7 | 119.8 | 102.6 | 111.9 | 107.2 | 96.7 | 101 | 97.7 | 98.2 | 125.6 | 115.7 | 90.3 | 107.45 | 125.6 | 90.3
2026-05-17 | 19:00:00.000 | 55.7 | 56.3 | 55.4 | 55.6 | 57.5 | 54.2 | 49.7 | 78.9 | 76.5 | 67.2 | 74.9 | 68.2 | 62.5083 | 78.9 | 49.7 | 51.3 | 52.5 | 54.4 | 50.9 | 57.7 | 64.5 | 65.7 | 68.1 | 67.5 | 63.1 | 59.2 | 64.2 | 59.925 | 68.1 | 50.9 | 80.6 | 78.6 | 67.5 | 73.7 | 70.7 | 65.2 | 66.6 | 65.5 | 68.6 | 83.9 | 76.1 | 63.8 | 71.7333 | 83.9 | 63.8
2026-05-17 | 19:15:00.000 | 30.2 | 30.2 | 28.9 | 29.7 | 30.8 | 28.9 | 28.5 | 42.9 | 41.2 | 38.6 | 40.9 | 37.2 | 34 | 42.9 | 28.5 | 28.6 | 29 | 29.8 | 26.8 | 31.9 | 34.1 | 34.9 | 36.2 | 35.7 | 31.9 | 31.2 | 34.5 | 32.05 | 36.2 | 26.8 | 45.3 | 42 | 37.5 | 41.7 | 40.2 | 34.1 | 36.8 | 34.4 | 37.8 | 47.4 | 41.3 | 33.5 | 39.3333 | 47.4 | 33.5
2026-05-17 | 19:30:00.000 | 18.9 | 19 | 18.6 | 19.3 | 19.5 | 17.7 | 19.2 | 28.7 | 27.8 | 25.7 | 27.1 | 24.3 | 22.15 | 28.7 | 17.7 | 18 | 19.3 | 19.2 | 16.2 | 19.5 | 21.1 | 22 | 22.6 | 22.2 | 20.6 | 19.3 | 21.2 | 20.1 | 22.6 | 16.2 | 29.5 | 28.8 | 24.2 | 26.3 | 25.1 | 22.1 | 22.8 | 22.6 | 24.7 | 30.9 | 27.3 | 21.7 | 25.5 | 30.9 | 21.7
2026-05-17 | 19:45:00.000 | 9.5 | 9.5 | 9.2 | 9.8 | 9.9 | 9.4 | 10.4 | 14.8 | 14.3 | 13.1 | 13.7 | 12.5 | 11.3417 | 14.8 | 9.2 | 9.1 | 10.4 | 10.1 | 8.5 | 10.3 | 11.2 | 12 | 12.8 | 12.9 | 12.9 | 12.5 | 13.9 | 11.3833 | 13.9 | 8.5 | 14.7 | 15.2 | 12.7 | 13.7 | 13.2 | 11.1 | 12 | 11.7 | 12.7 | 16.3 | 13.5 | 11.1 | 13.1583 | 16.3 | 11.1
2026-05-17 | 20:00:00.000 | 4.9 | 4.8 | 4.8 | 4.9 | 5.1 | 4.9 | 4.7 | 6.3 | 6.1 | 5.7 | 5.9 | 5.7 | 5.3167 | 6.3 | 4.7 | 4.9 | 5 | 5 | 4.8 | 5.8 | 6.1 | 6.6 | 6.8 | 7 | 6.7 | 6.6 | 7.1 | 6.0333 | 7.1 | 4.8 | 6.1 | 5.9 | 5.2 | 5.6 | 5.5 | 4.6 | 4.9 | 4.8 | 5.1 | 6.3 | 5.7 | 4.5 | 5.35 | 6.3 | 4.5
2026-05-17 | 20:15:00.000 | 1.9 | 1.6 | 2 | 2 | 2 | 2.1 | 2 | 2.6 | 2.5 | 2.4 | 2.5 | 2.4 | 2.1667 | 2.6 | 1.6 | 2 | 2 | 1.9 | 1.9 | 2.2 | 2.5 | 2.6 | 2.6 | 2.7 | 2.5 | 2.5 | 2.7 | 2.3417 | 2.7 | 1.9 | 2.6 | 2.2 | 2.2 | 2.4 | 2.5 | 2.1 | 2.1 | 2.2 | 2.2 | 2.4 | 2.4 | 1.9 | 2.2667 | 2.6 | 1.9
2026-05-17 | 20:30:00.000 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.2 | 0.3 | 0.4 | 0.4 | 0.2 | 0.4 | 0.4 | 0.3 | 0.5 | 0.1 | 0.3 | 0.3 | 0.7 | 0.3 | 0.7 | 0.4 | 0.4 | 0.6 | 0.5 | 0.4 | 0.4 | 0.7 | 0.475 | 0.7 | 0.3 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.3 | 0.475 | 0.6 | 0.3
2026-05-17 | 20:45:00.000 | 0.1 | 0 | 0.1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11818 | 0.3 | 0 | 0.1 | 0.1 | 0.6 | 0.1 | 0.3 | 0.1 | 0.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.4 | 0.20833 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0.11667 | 0.3 | 0.1
2026-05-17 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 | 0.15 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0
2026-05-17 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-17 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320