## PR_Calc
PR CALCULATION
01 MAGGIO 2026 | [52 empty] | 1 May 2026 PR Calculation
Total VALUES | [51 empty] | 96 | Total VALUES (4 values for each hour) | 96
PVSyst PR for current month | [51 empty] | 0.897 | Total values with POA>50 | 50
RAW PR | [51 empty] | 0.84911 | PVSyst PR for current month | 89.7
Irradiance Acceptance Rate [%] | [51 empty] | 0.03 | RAW PR (calculated with each power and POA value) [%] | 84.9107
Irradiance Minimum Value Accepted for calculation [%] | [51 empty] | 50 | Average of each PR [%] | 84.9455
NOMINAL VALUES | [52 empty] | PR from SCADA [%] | 37.5294
TX.INV | [13 empty] | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 1.10 | 1.11 | 1.12 |  | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 |  | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 3.10 | 3.11 | 3.12 |  | Irradiance Acceptance Rate (for average between sensors)[%] | 3
Potenza nominale DC | [13 empty] | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 343.75 | 359.375 | 359.375 | 359.375 | 359.375 | 343.75 |  | 328.125 | 343.75 | 343.75 | 328.125 | 328.125 | 359.375 | 343.75 | 359.375 | 359.375 | 343.75 | 359.375 | 359.375 |  | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 359.375 | 328.125 |  | Irradiance Minimum Value Accepted for calculation | 50
Potenza nominale AC | [13 empty] | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Dati | ORA | Irradiance TX1 [W/m2] A | Irradiance TX1 [KWh/m2] A | Irradiance TX3 [W/m2] B | Irradiance TX3 [KWh/m2] B | Irradiance Avg [KWh/m2] C = (A-B)/2 | Irradiance Average>50 [W/m2] | Irradiance Conditional MAX [KWh/m2] | Difference [%] (B-A)/C | Meter Reading (Previous day) D | Meter Reading (Current day) E | Energia attiva prod. (export meter) [kWh] F = (E - D)*1000 | Potenza Attiva Limit Ratio | Inverter status TX1-INV-1 | Inverter status TX1-INV-2 | Inverter status TX1-INV-3 | Inverter status TX1-INV-4 | Inverter status TX1-INV-5 | Inverter status TX1-INV-6 | Inverter status TX1-INV-7 | Inverter status TX1-INV-8 | Inverter status TX1-INV-9 | Inverter status TX1-INV-10 | Inverter status TX1-INV-11 | Inverter status TX1-INV-12 | Enegy Loss for TX1 kW/H | Inverter status TX2-INV-1 | Inverter status TX2-INV-2 | Inverter status TX2-INV-3 | Inverter status TX2-INV-4 | Inverter status TX2-INV-5 | Inverter status TX2-INV-6 | Inverter status TX2-INV-7 | Inverter status TX2-INV-8 | Inverter status TX2-INV-9 | Inverter status TX2-INV-10 | Inverter status TX2-INV-11 | Inverter status TX2-INV-12 | Enegy Loss for TX2 kW/H | Inverter status TX3-INV-1 | Inverter status TX3-INV-2 | Inverter status TX3-INV-3 | Inverter status TX3-INV-4 | Inverter status TX3-INV-5 | Inverter status TX3-INV-6 | Inverter status TX3-INV-7 | Inverter status TX3-INV-8 | Inverter status TX3-INV-9 | Inverter status TX3-INV-10 | Inverter status TX3-INV-11 | Inverter status TX3-INV-12 | Enegy Loss for TX3 kW/H
2026-05-01 | 00:00:00.000 | -1.5 | -0.000375 | -1.1 | -0.000275 | -0.000325 | 0 | -0.000325 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 00:15:00.000 | -2 | -0.0005 | -1.9 | -0.000475 | -0.0004875 | 0 | -0.0004875 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 00:30:00.000 | -1.1 | -0.000275 | -0.8 | -0.0002 | -0.0002375 | 0 | -0.0002375 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 00:45:00.000 | -1 | -0.00025 | -0.4 | -0.0001 | -0.000175 | 0 | -0.000175 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:00:00.000 | -0.5 | -0.000125 | -0.3 | -7.5e-05 | -0.0001 | 0 | -0.0001 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:15:00.000 | -0.4 | -0.0001 | -0.2 | -5e-05 | -7.5e-05 | 0 | -7.5e-05 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:30:00.000 | -0.7 | -0.000175 | -0.5 | -0.000125 | -0.00015 | 0 | -0.00015 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:00:00.000 | -1.8 | -0.00045 | -1.5 | -0.000375 | -0.0004125 | 0 | -0.0004125 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:15:00.000 | -1.9 | -0.000475 | -1.1 | -0.000275 | -0.000375 | 0 | -0.000375 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:00:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:15:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:00:00.000 | -0.8 | -0.0002 | -0.5 | -0.000125 | -0.0001625 | 0 | -0.0001625 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:15:00.000 | -1 | -0.00025 | -0.8 | -0.0002 | -0.000225 | 0 | -0.000225 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:30:00.000 | -0.9 | -0.000225 | -1 | -0.00025 | -0.0002375 | 0 | -0.0002375 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:00:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:15:00.000 | -1.2 | -0.0003 | -1 | -0.00025 | -0.000275 | 0 | -0.000275 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:30:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:45:00.000 | -1 | -0.00025 | -1 | -0.00025 | -0.00025 | 0 | -0.00025 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 06:00:00.000 | -0.6 | -0.00015 | -0.7 | -0.000175 | -0.0001625 | 0 | -0.0001625 | 0 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 06:15:00.000 | 3 | 0.00075 | 3.1 | 0.000775 | 0.0007625 | 0 | 0.0007625 | 0.032787 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 06:30:00.000 | 13.7 | 0.003425 | 13.5 | 0.003375 | 0.0034 | 0 | 0.0034 | 0.014706 | 30098.6 | 30098.6 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 06:45:00.000 | 41.9 | 0.010475 | 41.9 | 0.010475 | 0.010475 | 0 | 0.010475 | 0 | 30098.6 | 30098.7 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 07:00:00.000 | 79.8 | 0.01995 | 80.5 | 0.020125 | 0.020037 | 80.15 | 0.020125 | 0.0087336 | 30098.7 | 30098.8 | 100 | 0.876 | 5.1182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 07:15:00.000 | 133.2 | 0.0333 | 138.9 | 0.034725 | 0.034013 | 136.05 | 0.034725 | 0.041896 | 30098.8 | 30099 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 07:30:00.000 | 221.9 | 0.055475 | 226.4 | 0.0566 | 0.056038 | 224.15 | 0.0566 | 0.020076 | 30099 | 30099.5 | 500 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 07:45:00.000 | 334.2 | 0.08355 | 329.8 | 0.08245 | 0.083 | 332 | 0.08355 | 0.013253 | 30099.5 | 30100.3 | 800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 08:00:00.000 | 329.8 | 0.08245 | 344.6 | 0.08615 | 0.0843 | 337.2 | 0.08615 | 0.043891 | 30100.3 | 30101.2 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 08:15:00.000 | 243.6 | 0.0609 | 274.5 | 0.068625 | 0.064763 | 259.05 | 0.068625 | 0.11928 | 30101.2 | 30102.1 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 08:30:00.000 | 535.5 | 0.13387 | 560.8 | 0.1402 | 0.13704 | 548.15 | 0.1402 | 0.046155 | 30102.1 | 30103.3 | 1200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 08:45:00.000 | 647.9 | 0.16198 | 675.5 | 0.16887 | 0.16542 | 661.7 | 0.16887 | 0.041711 | 30103.3 | 30105.1 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 09:00:00.000 | 760 | 0.19 | 760.4 | 0.1901 | 0.19005 | 760.2 | 0.1901 | 0.00052618 | 30105.1 | 30107.1 | 2000 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 09:15:00.000 | 793.1 | 0.19828 | 763 | 0.19075 | 0.19451 | 778.05 | 0.19828 | 0.038686 | 30107.1 | 30109.4 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 09:30:00.000 | 590.3 | 0.14757 | 669.1 | 0.16728 | 0.15742 | 629.7 | 0.16728 | 0.12514 | 30109.4 | 30111.3 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 09:45:00.000 | 911.1 | 0.22778 | 874.7 | 0.21868 | 0.22323 | 892.9 | 0.22778 | 0.040766 | 30111.3 | 30113.4 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 10:00:00.000 | 850.2 | 0.21255 | 803.3 | 0.20082 | 0.20669 | 826.75 | 0.21255 | 0.056728 | 30113.4 | 30115.2 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 10:15:00.000 | 882.5 | 0.22062 | 865.1 | 0.21627 | 0.21845 | 873.8 | 0.22062 | 0.019913 | 30115.2 | 30117.6 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 10:30:00.000 | 822.1 | 0.20553 | 791.9 | 0.19797 | 0.20175 | 807 | 0.20553 | 0.037423 | 30117.6 | 30119.7 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 10:45:00.000 | 960 | 0.24 | 943.6 | 0.2359 | 0.23795 | 951.8 | 0.24 | 0.017231 | 30119.7 | 30122.1 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 11:00:00.000 | 545.8 | 0.13645 | 547.5 | 0.13687 | 0.13666 | 546.65 | 0.13687 | 0.0031099 | 30122.1 | 30123.9 | 1800 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 11:15:00.000 | 986.5 | 0.24663 | 942.7 | 0.23568 | 0.24115 | 964.6 | 0.24663 | 0.045407 | 30123.9 | 30125.8 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 11:30:00.000 | 1016.6 | 0.25415 | 959.5 | 0.23988 | 0.24701 | 988.05 | 0.25415 | 0.057791 | 30125.8 | 30128.1 | 2300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 11:45:00.000 | 928.8 | 0.2322 | 905.3 | 0.22632 | 0.22926 | 917.05 | 0.2322 | 0.025626 | 30128.1 | 30130.5 | 2400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 12:00:00.000 | 981 | 0.24525 | 944.2 | 0.23605 | 0.24065 | 962.6 | 0.24525 | 0.03823 | 30130.5 | 30131.6 | 1100 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288
2026-05-01 | 12:15:00.000 | 806.2 | 0.20155 | 792.1 | 0.19803 | 0.19979 | 799.15 | 0.20155 | 0.017644 | 30131.6 | 30131.6 | 0 | 0.0007 | 61.5472 | 61.5472 | 61.5472 | 61.5472 | 61.5472 | 61.5472 | 61.5472 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 61.5472 | 749.7673 | 58.7471 | 61.5472 | 61.5472 | 58.7471 | 58.7471 | 64.3474 | 61.5472 | 64.3474 | 64.3474 | 61.5472 | 64.3474 | 64.3474 | 744.167 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 64.3474 | 58.7471 | 766.5682
2026-05-01 | 12:30:00.000 | 945.3 | 0.23632 | 934.4 | 0.2336 | 0.23496 | 939.85 | 0.23632 | 0.011598 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 69.1001 | 70.024 | 70.024 | 69.1001 | 69.1001 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 837.5162 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 69.1001 | 839.3641
2026-05-01 | 12:45:00.000 | 912.4 | 0.2281 | 983 | 0.24575 | 0.23692 | 947.7 | 0.24575 | 0.074496 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 69.6777 | 70.024 | 70.024 | 69.6777 | 69.6777 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 839.2491 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 69.6777 | 839.9417
2026-05-01 | 13:00:00.000 | 880.2 | 0.22005 | 853.5 | 0.21338 | 0.21671 | 866.85 | 0.22005 | 0.030801 | 30131.6 | 30131.6 | 0 | 0.0007 | 66.7659 | 66.7659 | 66.7659 | 66.7659 | 66.7659 | 66.7659 | 66.7659 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 66.7659 | 813.3408 | 63.7286 | 66.7659 | 66.7659 | 63.7286 | 63.7286 | 69.8033 | 66.7659 | 69.8033 | 69.8033 | 66.7659 | 69.8033 | 69.8033 | 807.2661 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 69.8033 | 63.7286 | 831.565
2026-05-01 | 13:15:00.000 | 927.3 | 0.23182 | 897 | 0.22425 | 0.22804 | 912.15 | 0.23182 | 0.033218 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 67.0618 | 70.024 | 70.024 | 67.0618 | 67.0618 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 831.4015 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 67.0618 | 837.3258
2026-05-01 | 13:30:00.000 | 829.8 | 0.20745 | 811.7 | 0.20293 | 0.20519 | 820.75 | 0.20745 | 0.022053 | 30131.6 | 30131.6 | 0 | 0.0007 | 63.2123 | 63.2123 | 63.2123 | 63.2123 | 63.2123 | 63.2123 | 63.2123 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 63.2123 | 770.0507 | 60.3365 | 63.2123 | 63.2123 | 60.3365 | 60.3365 | 66.0881 | 63.2123 | 66.0881 | 66.0881 | 63.2123 | 66.0881 | 66.0881 | 764.2991 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 66.0881 | 60.3365 | 787.3057
2026-05-01 | 13:45:00.000 | 984.4 | 0.2461 | 951.5 | 0.23788 | 0.24199 | 967.95 | 0.2461 | 0.033989 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288
2026-05-01 | 14:00:00.000 | 963.8 | 0.24095 | 934.9 | 0.23372 | 0.23734 | 949.35 | 0.24095 | 0.030442 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 69.7991 | 70.024 | 70.024 | 69.7991 | 69.7991 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 839.6133 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 69.7991 | 840.0631
2026-05-01 | 14:15:00.000 | 864.2 | 0.21605 | 838.4 | 0.2096 | 0.21282 | 851.3 | 0.21605 | 0.030307 | 30131.6 | 30131.6 | 0 | 0.0007 | 65.5673 | 65.5673 | 65.5673 | 65.5673 | 65.5673 | 65.5673 | 65.5673 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 65.5673 | 798.7386 | 62.5844 | 65.5673 | 65.5673 | 62.5844 | 62.5844 | 68.5501 | 65.5673 | 68.5501 | 68.5501 | 65.5673 | 68.5501 | 68.5501 | 792.7729 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 68.5501 | 62.5844 | 816.6359
2026-05-01 | 14:30:00.000 | 907.9 | 0.22697 | 884 | 0.221 | 0.22399 | 895.95 | 0.22697 | 0.026676 | 30131.6 | 30131.6 | 0 | 0.0006 | 69.0171 | 69.0171 | 69.0171 | 69.0171 | 69.0171 | 69.0171 | 69.0171 | 70.032 | 70.032 | 70.032 | 70.032 | 69.0171 | 832.2652 | 65.8778 | 69.0171 | 69.0171 | 65.8778 | 65.8778 | 70.032 | 69.0171 | 70.032 | 70.032 | 69.0171 | 70.032 | 70.032 | 823.862 | 70.032 | 70.032 | 70.032 | 70.032 | 70.032 | 70.032 | 70.032 | 70.032 | 70.032 | 70.032 | 70.032 | 65.8778 | 836.2298
2026-05-01 | 14:45:00.000 | 976.1 | 0.24402 | 949 | 0.23725 | 0.24064 | 962.55 | 0.24402 | 0.028154 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288
2026-05-01 | 15:00:00.000 | 944.9 | 0.23622 | 921.9 | 0.23047 | 0.23335 | 933.4 | 0.23622 | 0.024641 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 68.6255 | 70.024 | 70.024 | 68.6255 | 68.6255 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 836.0924 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 68.6255 | 838.8895
2026-05-01 | 15:15:00.000 | 902.7 | 0.22568 | 881.8 | 0.22045 | 0.22306 | 892.25 | 0.22568 | 0.023424 | 30131.6 | 30131.6 | 0 | 0.0007 | 68.7239 | 68.7239 | 68.7239 | 68.7239 | 68.7239 | 68.7239 | 68.7239 | 70.024 | 70.024 | 70.024 | 70.024 | 68.7239 | 829.8874 | 65.5976 | 68.7239 | 68.7239 | 65.5976 | 65.5976 | 70.024 | 68.7239 | 70.024 | 70.024 | 68.7239 | 70.024 | 70.024 | 821.8084 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 65.5976 | 835.8616
2026-05-01 | 15:30:00.000 | 1027.6 | 0.2569 | 999.9 | 0.24998 | 0.25344 | 1013.75 | 0.2569 | 0.027324 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288
2026-05-01 | 15:45:00.000 | 987.4 | 0.24685 | 966.7 | 0.24168 | 0.24426 | 977.05 | 0.24685 | 0.021186 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288
2026-05-01 | 16:00:00.000 | 1007.6 | 0.2519 | 982.3 | 0.24557 | 0.24874 | 994.95 | 0.2519 | 0.025428 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288
2026-05-01 | 16:15:00.000 | 920.4 | 0.2301 | 901.4 | 0.22535 | 0.22773 | 910.9 | 0.2301 | 0.020858 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 66.9699 | 70.024 | 70.024 | 66.9699 | 66.9699 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 831.1256 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 66.9699 | 837.2339
2026-05-01 | 16:30:00.000 | 894.6 | 0.22365 | 869 | 0.21725 | 0.22045 | 881.8 | 0.22365 | 0.029032 | 30131.6 | 30131.6 | 0 | 0.0007 | 67.9184 | 67.9184 | 67.9184 | 67.9184 | 67.9184 | 67.9184 | 67.9184 | 70.024 | 70.024 | 70.024 | 70.024 | 67.9184 | 823.443 | 64.8286 | 67.9184 | 67.9184 | 64.8286 | 64.8286 | 70.024 | 67.9184 | 70.024 | 70.024 | 67.9184 | 70.024 | 70.024 | 816.2794 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 64.8286 | 835.0926
2026-05-01 | 16:45:00.000 | 898.4 | 0.2246 | 875.9 | 0.21898 | 0.22179 | 887.15 | 0.2246 | 0.025362 | 30131.6 | 30131.6 | 0 | 0.0007 | 68.3308 | 68.3308 | 68.3308 | 68.3308 | 68.3308 | 68.3308 | 68.3308 | 70.024 | 70.024 | 70.024 | 70.024 | 68.3308 | 826.7423 | 65.2223 | 68.3308 | 68.3308 | 65.2223 | 65.2223 | 70.024 | 68.3308 | 70.024 | 70.024 | 68.3308 | 70.024 | 70.024 | 819.1101 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 65.2223 | 835.4863
2026-05-01 | 17:00:00.000 | 992.6 | 0.24815 | 968.1 | 0.24203 | 0.24509 | 980.35 | 0.24815 | 0.024991 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288
2026-05-01 | 17:15:00.000 | 928.7 | 0.23218 | 944.3 | 0.23607 | 0.23412 | 936.5 | 0.23607 | 0.016658 | 30131.6 | 30131.6 | 0 | 0.0007 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 840.288 | 68.8536 | 70.024 | 70.024 | 68.8536 | 68.8536 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 836.7767 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 70.024 | 68.8536 | 839.1176
2026-05-01 | 17:30:00.000 | 791.3 | 0.19783 | 838 | 0.2095 | 0.20366 | 814.65 | 0.2095 | 0.057325 | 30131.6 | 30132.2 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 17:45:00.000 | 713.7 | 0.17843 | 771.1 | 0.19278 | 0.1856 | 742.4 | 0.19278 | 0.077317 | 30132.2 | 30134.3 | 2100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 18:00:00.000 | 600.1 | 0.15003 | 666.7 | 0.16668 | 0.15835 | 633.4 | 0.16668 | 0.10515 | 30134.3 | 30136.2 | 1900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 18:15:00.000 | 479.2 | 0.1198 | 548.8 | 0.1372 | 0.1285 | 514 | 0.1372 | 0.13541 | 30136.2 | 30137.8 | 1600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 18:30:00.000 | 373 | 0.09325 | 441.3 | 0.11033 | 0.10179 | 407.15 | 0.11033 | 0.16775 | 30137.8 | 30139.1 | 1300 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 18:45:00.000 | 262.7 | 0.065675 | 328 | 0.082 | 0.073838 | 295.35 | 0.082 | 0.22109 | 30139.1 | 30140 | 900 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 19:00:00.000 | 163.3 | 0.040825 | 218.4 | 0.0546 | 0.047713 | 190.85 | 0.0546 | 0.28871 | 30140 | 30140.6 | 600 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 19:15:00.000 | 112.6 | 0.02815 | 161.1 | 0.040275 | 0.034212 | 136.85 | 0.040275 | 0.3544 | 30140.6 | 30141 | 400 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 19:30:00.000 | 37.4 | 0.00935 | 61.8 | 0.01545 | 0.0124 | 0 | 0.0124 | 0.49194 | 30141 | 30141.2 | 200 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 19:45:00.000 | 21.6 | 0.0054 | 23.3 | 0.005825 | 0.0056125 | 0 | 0.0056125 | 0.075724 | 30141.2 | 30141.3 | 100 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 20:00:00.000 | 5.8 | 0.00145 | 6.3 | 0.001575 | 0.0015125 | 0 | 0.0015125 | 0.082645 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 20:15:00.000 | -0.7 | -0.000175 | -0.4 | -0.0001 | -0.0001375 | 0 | -0.0001375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 20:30:00.000 | -2.5 | -0.000625 | -2.2 | -0.00055 | -0.0005875 | 0 | -0.0005875 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 20:45:00.000 | -3 | -0.00075 | -2.7 | -0.000675 | -0.0007125 | 0 | -0.0007125 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 21:00:00.000 | -2.1 | -0.000525 | -1.2 | -0.0003 | -0.0004125 | 0 | -0.0004125 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 21:15:00.000 | -2 | -0.0005 | -1.7 | -0.000425 | -0.0004625 | 0 | -0.0004625 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 21:30:00.000 | -2 | -0.0005 | -1.4 | -0.00035 | -0.000425 | 0 | -0.000425 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 21:45:00.000 | -2 | -0.0005 | -1.5 | -0.000375 | -0.0004375 | 0 | -0.0004375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:00:00.000 | -2.4 | -0.0006 | -2.4 | -0.0006 | -0.0006 | 0 | -0.0006 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:15:00.000 | -1.8 | -0.00045 | -1.2 | -0.0003 | -0.000375 | 0 | -0.000375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:30:00.000 | -2 | -0.0005 | -1.6 | -0.0004 | -0.00045 | 0 | -0.00045 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:45:00.000 | -2 | -0.0005 | -2 | -0.0005 | -0.0005 | 0 | -0.0005 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:00:00.000 | -3 | -0.00075 | -2.4 | -0.0006 | -0.000675 | 0 | -0.000675 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:15:00.000 | -3 | -0.00075 | -3 | -0.00075 | -0.00075 | 0 | -0.00075 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:30:00.000 | -2.9 | -0.000725 | -2.2 | -0.00055 | -0.0006375 | 0 | -0.0006375 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:45:00.000 | -1.8 | -0.00045 | -2 | -0.0005 | -0.000475 | 0 | -0.000475 | 0 | 30141.3 | 30141.3 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PR for each inverter |  |  | 9.154 |  | 9.1537 | 9.1538 |  | 9.3469 |  |  |  | 42700 |  | 0.86311 | 0.8618 | 0.86103 | 0.86314 | 0.85908 | 0.85627 | 0.85588 | 0.84694 | 0.84278 | 0.83806 | 0.83717 | 0.86011 | 18213.3855 | 0.87401 | 0.85413 | 0.85234 | 0.86937 | 0.86954 | 0.82953 | 0.84885 | 0.82257 | 0.82246 | 0.84208 | 0.81834 | 0.81761 | 18123.3558 | 0.84818 | 0.84757 | 0.84824 | 0.84786 | 0.84482 | 0.84891 | 0.85369 | 0.84712 | 0.84791 | 0.85013 | 0.84645 | 0.88332 | 18298.6967
Note on D64: Abbasi: PPM was off for 1 hour.
Note on F64: Abbasi: PPM was off for 1 hour.

## Inverter_data
Dati | ORA | Active power TX1-INV-1 | Active power TX1-INV-2 | Active power TX1-INV-3 | Active power TX1-INV-4 | Active power TX1-INV-5 | Active power TX1-INV-6 | Active power TX1-INV-7 | Active power TX1-INV-8 | Active power TX1-INV-9 | Active power TX1-INV-10 | Active power TX1-INV-11 | Active power TX1-INV-12 | TX1 - Average Power | TX1 - Max Power | TX1 - Min Power | Active power TX2-INV-1 | Active power TX2-INV-2 | Active power TX2-INV-3 | Active power TX2-INV-4 | Active power TX2-INV-5 | Active power TX2-INV-6 | Active power TX2-INV-7 | Active power TX2-INV-8 | Active power TX2-INV-9 | Active power TX2-INV-10 | Active power TX2-INV-11 | Active power TX2-INV-12 | TX2 - Average Power | TX2 - Max Power | TX2 - Min Power | Active power TX3-INV-1 | Active power TX3-INV-2 | Active power TX3-INV-3 | Active power TX3-INV-4 | Active power TX3-INV-5 | Active power TX3-INV-6 | Active power TX3-INV-7 | Active power TX3-INV-8 | Active power TX3-INV-9 | Active power TX3-INV-10 | Active power TX3-INV-11 | Active power TX3-INV-12 | TX3 - Average Power | TX3 - Max Power | TX3 - Min Power
2026-05-01 | 00:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 00:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 00:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 00:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 01:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 02:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 03:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 04:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 05:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 06:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 06:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 06:30:00.000 | 0.9 | 0.7 | 1 | 1 | 1.6 | 0.8 | 1 | 1.1 | 1.3 | 0.9 | 1.1 | 1.4 | 1.0667 | 1.6 | 0.7 | 1.1 | 1 | 3.1 | 1.2 | 2.1 | 1.3 | 1.3 | 1.9 | 1.2 | 1.1 | 1.1 | 1.8 | 1.5167 | 3.1 | 1 | 2.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.1 | 1.1 | 0.9 | 1.1 | 1.2 | 1.225 | 2.1 | 0.9
2026-05-01 | 06:45:00.000 | 4.9 | 9.7 | 10 | 10.1 | 4.3 | 9.9 | 10 | 10 | 10.3 | 9.9 | 10.4 | 10.5 | 9.1667 | 10.5 | 4.3 | 9.7 | 9.9 | 10.2 | 9.9 | 9.8 | 10.4 | 10.5 | 10.8 | 10.8 | 10.2 | 10.9 | 10.7 | 10.3167 | 10.9 | 9.7 | 10.6 | 10.3 | 9.8 | 10 | 9.9 | 10.6 | 4.7 | 10.3 | 10 | 9.7 | 10.5 | 9.5 | 9.6583 | 10.6 | 4.7
2026-05-01 | 07:00:00.000 | 0 | 20.2 | 21.1 | 21.1 | 17 | 20.4 | 20.5 | 20.5 | 20.9 | 20.9 | 21.4 | 21.2 | 20.4727 | 21.4 | 0 | 19.6 | 19.3 | 20 | 20.3 | 20.1 | 21.3 | 21.1 | 21.6 | 21.9 | 20.7 | 22.1 | 21.1 | 20.7583 | 22.1 | 19.3 | 22.6 | 20.9 | 21.5 | 22.6 | 22.2 | 23.6 | 18.2 | 22.5 | 21.9 | 20.8 | 22.8 | 21.4 | 21.75 | 23.6 | 18.2
2026-05-01 | 07:15:00.000 | 26.4 | 38.1 | 39.8 | 39.3 | 39.6 | 38.2 | 37.9 | 38.9 | 39.4 | 39.3 | 40.5 | 39.7 | 38.0917 | 40.5 | 26.4 | 36.3 | 35.8 | 37.1 | 37.8 | 37.5 | 39.7 | 39.3 | 40.3 | 41.3 | 38.9 | 41.3 | 40.9 | 38.85 | 41.3 | 35.8 | 42 | 38.9 | 40.5 | 42.3 | 42 | 43.7 | 42.8 | 42 | 40.9 | 39.3 | 42.3 | 39.6 | 41.3583 | 43.7 | 38.9
2026-05-01 | 07:30:00.000 | 65.5 | 65.2 | 67.2 | 66.7 | 66.9 | 65.5 | 65.2 | 67.7 | 68 | 66 | 69.4 | 68.3 | 66.8 | 69.4 | 65.2 | 62.7 | 62.6 | 64.2 | 64.7 | 64.5 | 68.7 | 67.5 | 69.4 | 71 | 67.1 | 71.1 | 70.3 | 66.9833 | 71.1 | 62.6 | 71.7 | 67.7 | 69.7 | 71.8 | 70.8 | 72.9 | 71.5 | 70.4 | 69.4 | 67.2 | 71.8 | 66 | 70.075 | 72.9 | 66
2026-05-01 | 07:45:00.000 | 105.4 | 104.5 | 105.6 | 103.7 | 101.8 | 99.1 | 97.9 | 108.9 | 106.5 | 104.1 | 104.4 | 101.4 | 103.6083 | 108.9 | 97.9 | 92.9 | 93.8 | 93.8 | 92.1 | 91 | 102 | 97.5 | 99.2 | 99.3 | 93.2 | 96.8 | 94.2 | 95.4833 | 102 | 91 | 108.5 | 106.4 | 108.6 | 110.2 | 108.7 | 110.2 | 110.5 | 108.7 | 108.7 | 106.6 | 113 | 102.6 | 108.5583 | 113 | 102.6
2026-05-01 | 08:00:00.000 | 105.2 | 104.1 | 105.3 | 104.9 | 103.1 | 101.9 | 102.5 | 109.8 | 108.3 | 107.1 | 108.1 | 105.4 | 105.475 | 109.8 | 101.9 | 97.3 | 98.9 | 99.3 | 96.7 | 96.3 | 109.2 | 104.8 | 107.6 | 107.9 | 101.9 | 104.9 | 104.9 | 102.475 | 109.2 | 96.3 | 113.2 | 108.3 | 108.3 | 104.7 | 103.5 | 111 | 112.7 | 110.1 | 109.2 | 107.4 | 112.3 | 101.8 | 108.5417 | 113.2 | 101.8
2026-05-01 | 08:15:00.000 | 80 | 79.1 | 81.7 | 82.3 | 79.4 | 76.1 | 76.5 | 86.1 | 87.4 | 87.1 | 86.9 | 85.4 | 82.3333 | 87.4 | 76.1 | 73.5 | 76 | 76.2 | 74.6 | 74.9 | 91.3 | 86.4 | 88.6 | 87.8 | 82.5 | 85.2 | 86.6 | 81.9667 | 91.3 | 73.5 | 92.8 | 85.9 | 95.8 | 100.6 | 98.3 | 97.5 | 95 | 91.6 | 90.8 | 89.8 | 87.7 | 85 | 92.5667 | 100.6 | 85
2026-05-01 | 08:30:00.000 | 174.2 | 172.9 | 175.3 | 176.1 | 175.5 | 172.9 | 173.4 | 184.8 | 182.5 | 182.7 | 183 | 179.6 | 177.7417 | 184.8 | 172.9 | 166.2 | 167.4 | 171.9 | 168.3 | 168.8 | 185.7 | 178.2 | 183 | 183.5 | 175.1 | 183.2 | 181.2 | 176.0417 | 185.7 | 166.2 | 186.3 | 185.8 | 187.4 | 190.4 | 190.1 | 190.9 | 188.4 | 183.9 | 178.4 | 184 | 188.4 | 155.9 | 184.1583 | 190.9 | 155.9
2026-05-01 | 08:45:00.000 | 211.9 | 209.6 | 212.2 | 213.5 | 212.8 | 211.7 | 213.9 | 224.1 | 220.7 | 219.3 | 220.3 | 215.2 | 215.4333 | 224.1 | 209.6 | 203.3 | 210.5 | 210.4 | 203.5 | 204.2 | 223.5 | 212.6 | 220 | 219.3 | 202.4 | 218.4 | 215.9 | 212 | 223.5 | 202.4 | 222.4 | 221.8 | 223.4 | 226.8 | 226.8 | 227.4 | 228.5 | 222.1 | 221.9 | 220.9 | 217.1 | 206.5 | 222.1333 | 228.5 | 206.5
2026-05-01 | 09:00:00.000 | 242.2 | 238.6 | 240.2 | 241.3 | 240.2 | 239.4 | 243.9 | 255.1 | 248.3 | 244.4 | 245.3 | 241.4 | 243.3583 | 255.1 | 238.6 | 232 | 241.1 | 240.5 | 232.2 | 233.2 | 250.1 | 240.4 | 249.4 | 248.3 | 237.3 | 247.7 | 243.2 | 241.2833 | 250.1 | 232 | 250.5 | 252.2 | 252.6 | 256.6 | 256.4 | 256.1 | 259.3 | 251 | 251.7 | 251 | 254.4 | 233.5 | 252.1083 | 259.3 | 233.5
2026-05-01 | 09:15:00.000 | 235.5 | 245.3 | 246.5 | 255.5 | 255.2 | 254.7 | 259.4 | 270.2 | 267.2 | 263 | 261.9 | 255.8 | 255.85 | 270.2 | 235.5 | 237.4 | 255.1 | 252.7 | 241.4 | 239.8 | 261.7 | 247.3 | 246.8 | 253.5 | 241.5 | 246.9 | 241.4 | 247.125 | 261.7 | 237.4 | 256.2 | 255.1 | 253.5 | 254.8 | 252.6 | 246.6 | 260.2 | 252.9 | 256.8 | 257 | 255.2 | 220.2 | 251.7583 | 260.2 | 220.2
2026-05-01 | 09:30:00.000 | 185.3 | 176.8 | 178.4 | 187.1 | 189.2 | 191.8 | 192.8 | 190.6 | 191.8 | 189.8 | 190.3 | 190.4 | 187.8583 | 192.8 | 176.8 | 194 | 198.1 | 197.3 | 192.5 | 193.6 | 200.9 | 199.5 | 201.7 | 204.2 | 200.5 | 200.9 | 202.9 | 198.8417 | 204.2 | 192.5 | 195.4 | 196.5 | 191.7 | 207.9 | 198.2 | 195.7 | 191.2 | 193.6 | 192.6 | 187.3 | 195.2 | 206.2 | 195.9583 | 207.9 | 187.3
2026-05-01 | 09:45:00.000 | 271.6 | 270.9 | 271.3 | 269.1 | 257.3 | 250.3 | 240.2 | 269.6 | 261.4 | 253.1 | 244.8 | 236.6 | 258.0167 | 271.6 | 236.6 | 231.3 | 230.5 | 223.9 | 217.6 | 211.3 | 226.8 | 215.8 | 210.1 | 200.7 | 202.4 | 205.1 | 199.2 | 214.5583 | 231.3 | 199.2 | 246.9 | 251 | 263.7 | 263.7 | 263.9 | 262.6 | 275.4 | 270.2 | 259.4 | 265.8 | 268.6 | 261.2 | 262.7 | 275.4 | 246.9
2026-05-01 | 10:00:00.000 | 268.7 | 250.1 | 238 | 229.3 | 220.5 | 214.4 | 203.6 | 237.5 | 223.8 | 216.2 | 214.1 | 210.1 | 227.1917 | 268.7 | 203.6 | 193.5 | 194 | 191.5 | 188.4 | 188.4 | 207.5 | 180.9 | 199.5 | 198.1 | 193.7 | 191.9 | 191 | 193.2 | 207.5 | 180.9 | 223 | 230.6 | 227.1 | 245.6 | 260.6 | 277.9 | 276.2 | 275.2 | 267.6 | 248.4 | 240.3 | 263.7 | 253.0167 | 277.9 | 223
2026-05-01 | 10:15:00.000 | 263.5 | 263.8 | 263.1 | 260.1 | 258.4 | 262.5 | 267.4 | 256.9 | 261 | 260.8 | 262.8 | 263.7 | 262 | 267.4 | 256.9 | 265.4 | 270.4 | 269.7 | 265.8 | 261.8 | 260.9 | 252.6 | 251.3 | 250.3 | 239.4 | 249.7 | 249.9 | 257.2667 | 270.4 | 239.4 | 264.5 | 271.9 | 271.9 | 268.6 | 265.3 | 263.1 | 266.5 | 257.4 | 258.6 | 258.7 | 250.3 | 268.7 | 263.7917 | 271.9 | 250.3
2026-05-01 | 10:30:00.000 | 227.8 | 226.6 | 236.5 | 246.1 | 252 | 258 | 260.4 | 247.4 | 251.2 | 254.8 | 258.5 | 262.7 | 248.5 | 262.7 | 226.6 | 266.3 | 263.6 | 260.8 | 255.3 | 252.6 | 257.6 | 260.5 | 255.9 | 258.1 | 258.7 | 265 | 271.5 | 260.4917 | 271.5 | 252.6 | 250 | 247.9 | 244.9 | 215.8 | 213.6 | 216.6 | 224.3 | 226.8 | 226.1 | 231.5 | 237.6 | 146.8 | 223.4917 | 250 | 146.8
2026-05-01 | 10:45:00.000 | 268.8 | 272 | 269.3 | 272.6 | 275.7 | 276.7 | 275.9 | 277.4 | 278.3 | 271.6 | 271.8 | 273.1 | 273.6 | 278.3 | 268.8 | 273.6 | 276.3 | 276.2 | 278.7 | 280 | 271 | 271.4 | 273.3 | 272.6 | 271.3 | 272.3 | 269.4 | 273.8417 | 280 | 269.4 | 268.9 | 268.8 | 276.5 | 274.6 | 268.5 | 261.7 | 268.5 | 266.3 | 266.3 | 270.7 | 272.1 | 267.6 | 269.2083 | 276.5 | 261.7
2026-05-01 | 11:00:00.000 | 162.9 | 163.5 | 167.8 | 179.4 | 182.6 | 183 | 200.9 | 180.6 | 179.4 | 190.4 | 196.6 | 188.8 | 181.325 | 200.9 | 162.9 | 198.3 | 201.1 | 195.8 | 194.6 | 199.4 | 194.8 | 194.6 | 203.3 | 205.3 | 204.8 | 206 | 207.7 | 200.475 | 207.7 | 194.6 | 185.4 | 179.9 | 171.5 | 165 | 161 | 162.5 | 165.3 | 167.1 | 164.2 | 165 | 169.7 | 134.3 | 165.9083 | 185.4 | 134.3
2026-05-01 | 11:15:00.000 | 260.2 | 251.9 | 249.4 | 241.7 | 230.2 | 214.4 | 213.6 | 251.5 | 228.4 | 225.9 | 218.3 | 205.8 | 232.6083 | 260.2 | 205.8 | 199.1 | 203.6 | 197 | 184.9 | 176.3 | 201.8 | 190.6 | 187.9 | 181.8 | 174.6 | 175 | 171.6 | 187.0167 | 203.6 | 171.6 | 223 | 228.2 | 255.3 | 271.1 | 263 | 277.4 | 273.9 | 265 | 262.2 | 267.1 | 255.7 | 269.1 | 259.25 | 277.4 | 223
2026-05-01 | 11:30:00.000 | 279.5 | 279.6 | 271.3 | 265.2 | 263.7 | 264.7 | 265.2 | 262.9 | 270.5 | 273.7 | 261.7 | 269.1 | 268.925 | 279.6 | 261.7 | 264.4 | 264.5 | 261.2 | 258.4 | 256.5 | 271.2 | 268.8 | 269.6 | 271.3 | 266.3 | 263.8 | 255.3 | 264.275 | 271.3 | 255.3 | 272.9 | 273 | 273.1 | 271.7 | 275.2 | 274.5 | 275.1 | 273 | 274 | 273.5 | 257.6 | 271.4 | 272.0833 | 275.2 | 257.6
2026-05-01 | 11:45:00.000 | 270 | 268.6 | 263.4 | 268.4 | 251.5 | 258.2 | 265.8 | 267 | 266.8 | 259.9 | 261.7 | 265.9 | 263.9333 | 270 | 251.5 | 262.3 | 266.7 | 269 | 260.7 | 263.7 | 269.9 | 264.2 | 259.3 | 262.6 | 260.7 | 266.4 | 266.6 | 264.3417 | 269.9 | 259.3 | 274.2 | 267.9 | 272.1 | 268.2 | 266.7 | 268.2 | 270.7 | 265.3 | 261.8 | 270.9 | 266.3 | 259.2 | 267.625 | 274.2 | 259.2
2026-05-01 | 12:00:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 12:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 12:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 12:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 13:00:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 13:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 13:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 13:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 14:00:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 14:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 14:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 14:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 15:00:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 15:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 15:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 15:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 16:00:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 16:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 16:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 16:45:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 17:00:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 17:15:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2026-05-01 | 17:30:00.000 | 168.8 | 177.8 | 170.7 | 170.2 | 173.2 | 171.3 | 179.5 | 184.6 | 192.7 | 185.5 | 182.1 | 178.9 | 177.9417 | 192.7 | 168.8 | 159.8 | 170.9 | 174.4 | 163.2 | 165.3 | 174 | 169.6 | 176.3 | 170.2 | 170.2 | 174.6 | 176.4 | 170.4083 | 176.4 | 159.8 | 194.6 | 189.7 | 191.5 | 180.7 | 184.1 | 196.2 | 188.9 | 187 | 191.6 | 186.4 | 189.8 | 168.2 | 187.3917 | 196.2 | 168.2
2026-05-01 | 17:45:00.000 | 227.9 | 226.4 | 225.9 | 226.7 | 226.8 | 225.5 | 222.6 | 248.3 | 244.9 | 240.6 | 239.9 | 225.3 | 231.7333 | 248.3 | 222.6 | 211.9 | 223.9 | 220.6 | 210.4 | 214.4 | 228 | 217.6 | 222.3 | 224.6 | 214.5 | 221.3 | 223.6 | 219.425 | 228 | 210.4 | 256.5 | 257.1 | 253.4 | 252.6 | 239.4 | 239.9 | 254.1 | 246.9 | 252 | 257.5 | 254.8 | 221.8 | 248.8333 | 257.5 | 221.8
2026-05-01 | 18:00:00.000 | 193.8 | 192.8 | 192 | 193 | 193.2 | 191.2 | 181 | 214.7 | 210.6 | 207.4 | 207.5 | 192.5 | 197.475 | 214.7 | 181 | 181.4 | 191.3 | 188.9 | 179.2 | 182.6 | 193.7 | 185.3 | 190.1 | 190.9 | 181.8 | 186.9 | 189.3 | 186.7833 | 193.7 | 179.2 | 221.5 | 223.5 | 218.2 | 214.4 | 212.2 | 213.4 | 218.5 | 212.3 | 217.9 | 224.3 | 218.6 | 197.4 | 216.0167 | 224.3 | 197.4
2026-05-01 | 18:15:00.000 | 156.4 | 155.6 | 154.9 | 155.6 | 155.9 | 153.3 | 144.6 | 174 | 170.4 | 167.3 | 167.1 | 155.1 | 159.1833 | 174 | 144.6 | 145.8 | 152.1 | 152.2 | 143.3 | 144.9 | 154 | 147.9 | 151.8 | 151.8 | 143.7 | 146.4 | 148.2 | 148.5083 | 154 | 143.3 | 180.9 | 183.7 | 176.9 | 171.8 | 171.3 | 174.5 | 178.9 | 173.7 | 179 | 184.9 | 176.8 | 161.6 | 176.1667 | 184.9 | 161.6
2026-05-01 | 18:30:00.000 | 122.6 | 122 | 120.9 | 121.9 | 122.1 | 118.6 | 107.6 | 137.7 | 134.7 | 132.1 | 132 | 120.8 | 124.4167 | 137.7 | 107.6 | 113.8 | 118.7 | 118.3 | 110.7 | 111.6 | 118.5 | 114.3 | 113.2 | 116.5 | 109.7 | 110.6 | 112.9 | 114.0667 | 118.7 | 109.7 | 144.3 | 145.7 | 137.3 | 133.7 | 133.1 | 136.7 | 141.3 | 137.1 | 142.6 | 147.6 | 140.7 | 127.7 | 138.9833 | 147.6 | 127.7
2026-05-01 | 18:45:00.000 | 86.4 | 85.9 | 84.8 | 85.9 | 86.2 | 82.3 | 78.1 | 98.9 | 96.7 | 94.1 | 93.9 | 84.8 | 88.1667 | 98.9 | 78.1 | 79.3 | 83.1 | 82.2 | 76.3 | 77.1 | 81.3 | 78.9 | 81 | 79.9 | 74.7 | 74.1 | 76.3 | 78.6833 | 83.1 | 74.1 | 103.9 | 104.3 | 97 | 95.4 | 94.1 | 96.9 | 101.2 | 98.3 | 103.2 | 106.9 | 99.9 | 92.2 | 99.4417 | 106.9 | 92.2
2026-05-01 | 19:00:00.000 | 52.1 | 51.4 | 50.6 | 51.5 | 51.6 | 48.7 | 47.6 | 58.8 | 59.3 | 57.4 | 57.1 | 51.5 | 53.1333 | 59.3 | 47.6 | 46.9 | 47.7 | 48.5 | 44 | 44.7 | 47.5 | 46 | 47.3 | 46.3 | 43 | 41.5 | 43.5 | 45.575 | 48.5 | 41.5 | 65.1 | 65.5 | 60.5 | 57.8 | 58.8 | 60.2 | 63.3 | 59.1 | 65.3 | 68 | 61.7 | 57.9 | 61.9333 | 68 | 57.8
2026-05-01 | 19:15:00.000 | 33.8 | 33.2 | 32.7 | 33.8 | 34 | 31.7 | 32.7 | 42.2 | 41 | 37.6 | 38.9 | 34.1 | 35.475 | 42.2 | 31.7 | 29.9 | 32.3 | 31 | 27.2 | 28.1 | 29.1 | 28 | 28 | 27.6 | 25.3 | 23.4 | 25.5 | 27.95 | 32.3 | 23.4 | 43.6 | 45.2 | 40.9 | 40.1 | 39.4 | 36.7 | 41.9 | 40.7 | 44.7 | 47.6 | 40 | 39 | 41.65 | 47.6 | 36.7
2026-05-01 | 19:30:00.000 | 10.5 | 10.4 | 10.3 | 10.6 | 10.5 | 10 | 11.3 | 13.8 | 13.5 | 12.8 | 12.6 | 11.1 | 11.45 | 13.8 | 10 | 9.3 | 10.3 | 9.8 | 8.8 | 9.4 | 10 | 10.2 | 10.9 | 11 | 11.1 | 11.5 | 12.2 | 10.375 | 12.2 | 8.8 | 14.4 | 15.4 | 13.4 | 13.6 | 13.3 | 12.1 | 12.9 | 13.1 | 14.7 | 16.3 | 13.3 | 12.8 | 13.775 | 16.3 | 12.1
2026-05-01 | 19:45:00.000 | 6 | 5.7 | 5.7 | 5.7 | 5.9 | 5.7 | 5.2 | 6.2 | 6.1 | 5.8 | 5.6 | 5.4 | 5.75 | 6.2 | 5.2 | 5.7 | 5.6 | 5.4 | 5.6 | 5.9 | 6 | 6.1 | 6.4 | 6.7 | 6.6 | 6.7 | 6.8 | 6.125 | 6.8 | 5.4 | 5.9 | 6 | 5.8 | 5.7 | 5.7 | 5.4 | 5.6 | 5.5 | 6 | 6.5 | 5.7 | 5.6 | 5.7833 | 6.5 | 5.4
2026-05-01 | 20:00:00.000 | 2 | 1.9 | 2 | 2 | 2 | 2.2 | 2 | 2.2 | 2.1 | 2.2 | 2.1 | 2 | 2.0583 | 2.2 | 1.9 | 1.9 | 2 | 1.8 | 1.9 | 1.9 | 2.1 | 2 | 2.2 | 2.2 | 2 | 2.2 | 2.1 | 2.025 | 2.2 | 1.8 | 2.2 | 1.9 | 2.1 | 2.1 | 2.2 | 2 | 2 | 2.1 | 2.2 | 2.2 | 2.2 | 1.9 | 2.0917 | 2.2 | 1.9
2026-05-01 | 20:15:00.000 | 0.2 | 0.1 | 0.4 | 0.4 | 0.6 | 0.4 | 0.4 | 0.5 | 0.5 | 0.3 | 0.2 | 0.6 | 0.38333 | 0.6 | 0.1 | 0.4 | 0.5 | 0.2 | 0.5 | 0.7 | 0.5 | 0.5 | 0.4 | 0.6 | 0.4 | 0.2 | 0.7 | 0.46667 | 0.7 | 0.2 | 0.6 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.5 | 0.6 | 0.6 | 0.4 | 0.53333 | 0.7 | 0.4
2026-05-01 | 20:30:00.000 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.125 | 0.3 | 0.1 | 0.1 | 0.1 | 0.8 | 0.1 | 0.4 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.5 | 0.225 | 0.8 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.10833 | 0.2 | 0.1
2026-05-01 | 20:45:00.000 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0.2 | 0.15 | 0.3 | 0 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0
2026-05-01 | 21:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 21:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 21:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 21:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 22:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:00:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:15:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:30:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-01 | 23:45:00.000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Nominal_Values
CAMPO FV | SOTTOCAMPI INVERTER BOX | Potenza nominale DC inverter [kVA] | Potenza nominale AC inverter [kVA]
T1 | 1.1 | 343.75 | 320
| 1.2 | 343.75 | 320
| 1.3 | 343.75 | 320
| 1.4 | 343.75 | 320
| 1.5 | 343.75 | 320
| 1.6 | 343.75 | 320
| 1.7 | 343.75 | 320
| 1.8 | 359.375 | 320
| 1.9 | 359.375 | 320
| 1.10 | 359.375 | 320
| 1.11 | 359.375 | 320
| 1.12 | 343.75 | 320
T2 | 2.1 | 328.125 | 320
| 2.2 | 343.75 | 320
| 2.3 | 343.75 | 320
| 2.4 | 328.125 | 320
| 2.5 | 328.125 | 320
| 2.6 | 359.375 | 320
| 2.7 | 343.75 | 320
| 2.8 | 359.375 | 320
| 2.9 | 359.375 | 320
| 2.10 | 343.75 | 320
| 2.11 | 359.375 | 320
| 2.12 | 359.375 | 320
T3 | 3.1 | 359.375 | 320
| 3.2 | 359.375 | 320
| 3.3 | 359.375 | 320
| 3.4 | 359.375 | 320
| 3.5 | 359.375 | 320
| 3.6 | 359.375 | 320
| 3.7 | 359.375 | 320
| 3.8 | 359.375 | 320
| 3.9 | 359.375 | 320
| 3.10 | 359.375 | 320
| 3.11 | 359.375 | 320
| 3.12 | 328.125 | 320